## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | COOS
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2023-08-01
System Name: | Camp Myrtlewood |  |  | ID#: 41 | 90861 |  | WTP : TP - | SSF/Chlorination
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  | 0.1
2 |  |  | 0.3
3 |  |  | 0.1
4 |  |  | 0.1
5 |  |  | 0.1
6 |  |  | 0.1
7 |  |  | 0.1
8 |  |  | 0.1
9 |  |  | 0.1
10 |  |  | 0.1
11 |  |  | 0.1
12 |  |  | 0.1
13 |  |  | 0.1
14 |  |  | 0.1
15 |  |  | 0.2
16 |  |  | 0.1
17 |  |  | 0.1
18 |  |  | 0.3
19 |  |  | 0.2
20 |  |  | 0.1
21 |  |  | 0.1
22 |  |  | 0.1
23 |  |  | 0.1
24 |  |  | 0.1
25 |  |  | 0.2
26 |  |  | 0.1
27 |  |  | 0.1
28 |  |  | 0.3
29 |  |  | 0.1
30 |  |  | off
31 |  |  | off
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes |  | Yes
Notes: The system was shut off Aug 30-31 because all staff were off-site. |  |  |  |  | PRINTED NAME: Shauna Danielson
[5 empty] | SIGNATURE: Shauna Danielson |  |  | DATE: 9/2/2023
[5 empty] | PHONE #: (541)572.5307 |  |  | CERT #: N/A
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | SSF/Chlorination
System Name: | Camp Myrtlewood |  | ID#: 41 | 90861 | Month/Year: |  | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1 | 43 | 43 | 17.7 | 7.94 | 32.2318 | YES | 0.07
2 | 1 | 43 | 43 | 17.1 | 7.95 | 33.6704 | YES | 0.15
3 | 1 | 43 | 43 | 17.5 | 7.9 | 32.1843 | YES | 0.17
4 | 1 | 43 | 43 | 18.4 | 7.92 | 30.5347 | YES | 0.15
5 | 1 | 43 | 43 | 18.5 | 7.96 | 30.7846 | YES | 0.13
6 | 1 | 43 | 43 | 20.3 | 7.89 | 26.5939 | YES | 0.08
7 | 1 | 43 | 43 | 20 | 7.81 | 26.338 | YES | 0.08
8 | 1 | 43 | 43 | 19.5 | 7.84 | 27.5405 | YES | 0.11
9 | 1 | 43 | 43 | 16 | 7.89 | 35.4328 | YES | 0.18
10 | 1 | 43 | 43 | 20.6 | 7.9 | 26.1618 | YES | 0.22
11 | 1 | 43 | 43 | 18.2 | 7.93 | 31.0598 | YES | 0.24
12 | 1 | 43 | 43 | 17.9 | 7.9 | 31.3373 | YES | 0.28
13 | 1 | 43 | 43 | 17.9 | 7.91 | 31.4536 | YES | 0.23
14 | 1 | 43 | 43 | 19.6 | 7.86 | 27.5609 | YES | 0.24
15 | 1 | 43 | 43 | 20.7 | 7.89 | 25.8904 | YES | 0.23
16 | 1 | 43 | 43 | 20.3 | 7.88 | 26.4951 | YES | 0.25
17 | 1 | 43 | 43 | 20.5 | 7.87 | 26.0452 | YES | 0.29
18 | 1 | 43 | 43 | 21.5 | 7.88 | 24.4458 | YES | 0.16
19 | 1 | 43 | 43 | 17.2 | 8.02 | 34.3239 | YES | 0.29
20 | 1 | 43 | 43 | 17.9 | 7.98 | 32.2795 | YES | 0.31
21 | 1 | 43 | 43 | 18.5 | 7.97 | 30.8989 | YES | 0.22
22 | 1 | 43 | 43 | 18.9 | 7.92 | 29.5321 | YES | 0.38
23 | 1 | 43 | 43 | 16.4 | 8 | 35.9332 | YES | 0.04
24 | 1 | 43 | 43 | 16.1 | 8.03 | 37.0649 | YES | 0.12
25 | 1 | 43 | 43 | 18.8 | 7.91 | 29.62 | YES | 0.08
26 | 1 | 43 | 43 | 17.7 | 7.92 | 31.9941 | YES | 0.04
27 | 1 | 43 | 43 | 18.8 | 7.88 | 29.2921 | YES | 0.03
28 | 1 | 43 | 43 | 18.2 | 7.86 | 30.2643 | YES | 0.02
29 | 1 | 43 | 43 | 18 | 7.88 | 30.8992 | YES | 0.03
30
31
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2