## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Linn
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2021-01-01
System Name: | Big Lake Youth Camp |  |  | ID#: 41 | 90958 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 10 | 6 | 4 | 30 | 0.17 | 0.17
2 | 10 | 6 | 4 | 30 | 0.15 | 0.15
3 | 10 | 6 | 4 | 30 | 0.16 | 0.16
4 | 10 | 6 | 4 | 30 | 0.14 | 0.14
5 | 10 | 6 | 4 | 30 | 0.18 | 0.18
6 | 10 | 6 | 4 | 30 | 0.16 | 0.16
7 | 10 | 6 | 4 | 30 | 0.17 | 0.17
8 | 10 | 6 | 4 | 30 | 0.15 | 0.15
9 | 10 | 6 | 4 | 30 | 0.13 | 0.13
10 | 10 | 6 | 4 | 30 | 0.15 | 0.15
11 | 10 | 6 | 4 | 30 | 0.16 | 0.16
12 | 10 | 6 | 4 | 30 | 0.13 | 0.13
13 | 12 | 6 | 6 | 30 | 0.15 | 0.15
14 | 12 | 6 | 6 | 30 | 0.16 | 0.16
15 | 12 | 6 | 6 | 30 | 0.14 | 0.14
16 | 12 | 6 | 6 | 30 | 0.12 | 0.12
17 | 12 | 6 | 6 | 30 | 0.13 | 0.13
18 | 12 | 6 | 6 | 30 | 0.15 | 0.15
19 | 15 | 6 | 9 | 30 | 0.17 | 0.17
20 | 15 | 6 | 9 | 30 | 0.16 | 0.16
21 | 15 | 6 | 9 | 30 | 0.14 | 0.14
22 | 15 | 6 | 9 | 30 | 0.13 | 0.13
23 | 20 | 6 | 14 | 30 | 0.15 | 0.15
24 | 20 | 6 | 14 | 30 | 0.17 | 0.17
25 | 20 | 6 | 14 | 30 | 0.13 | 0.13
26 | 20 | 6 | 14 | 30 | 0.12 | 0.12
27 | 20 | 6 | 14 | 30 | 0.15 | 0.15
28 | 25 | 6 | 19 | 30 | 0.14 | 0.14
29 | 25 | 6 | 19 | 30 | 0.16 | 0.16
30 | 25 | 6 | 19 | 30 | 0.14 | 0.14
31 | 25 | 6 | 19 | 30 | 0.15 | 0.15
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME:Ross von Pohle
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE:Ross von Pohle |  | DATE:02/10/2021
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: (503)850-3576 |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Big Lake Youth Camp |  | ID#: 41 | 90958 | Month/Year: | 2021-01-01 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.6 | 84 | 50.4 | 7.3 | 7.72 | 28.45 | Yes | 36
2 | 0.6 | 84 | 50.4 | 7.3 | 7.7 | 28.246 | Yes | 36
3 | 0.6 | 84 | 50.4 | 7.3 | 7.71 | 28.3478 | Yes | 36
4 | 0.6 | 84 | 50.4 | 7.3 | 7.68 | 28.0435 | Yes | 36
5 | 0.6 | 84 | 50.4 | 7.3 | 7.66 | 27.8426 | Yes | 36
6 | 0.6 | 84 | 50.4 | 7.3 | 7.69 | 28.1445 | Yes | 36
7 | 0.6 | 84 | 50.4 | 7.3 | 7.65 | 27.7427 | Yes | 36
8 | 0.6 | 84 | 50.4 | 7.1 | 7.64 | 28.0186 | Yes | 36
9 | 0.6 | 84 | 50.4 | 7.1 | 7.66 | 28.2209 | Yes | 36
10 | 0.6 | 84 | 50.4 | 7.1 | 7.62 | 27.8179 | Yes | 36
11 | 0.5 | 84 | 42 | 7.1 | 7.6 | 27.302 | Yes | 36
12 | 0.5 | 84 | 42 | 7.1 | 7.59 | 27.2042 | Yes | 36
13 | 0.5 | 84 | 42 | 7.1 | 7.57 | 27.0098 | Yes | 36
14 | 0.5 | 84 | 42 | 7.1 | 7.6 | 27.302 | Yes | 36
15 | 0.5 | 84 | 42 | 7 | 7.55 | 26.9978 | Yes | 36
16 | 0.5 | 84 | 42 | 7 | 7.51 | 26.6137 | Yes | 36
17 | 0.5 | 84 | 42 | 7 | 7.53 | 26.805 | Yes | 36
18 | 0.5 | 84 | 42 | 7 | 7.49 | 26.4239 | Yes | 36
19 | 0.5 | 84 | 42 | 7 | 7.5 | 26.5186 | Yes | 36
20 | 0.5 | 84 | 42 | 7 | 7.51 | 26.6137 | Yes | 36
21 | 0.5 | 84 | 42 | 7 | 7.48 | 26.3295 | Yes | 36
22 | 0.5 | 84 | 42 | 7 | 7.46 | 26.1419 | Yes | 36
23 | 0.5 | 84 | 42 | 7 | 7.49 | 26.4239 | Yes | 36
24 | 0.5 | 84 | 42 | 7 | 7.48 | 26.3295 | Yes | 36
25 | 0.5 | 84 | 42 | 7 | 7.47 | 26.2355 | Yes | 36
26 | 0.4 | 84 | 33.6 | 7 | 7.45 | 25.7514 | Yes | 36
27 | 0.4 | 84 | 33.6 | 7 | 7.44 | 25.6596 | Yes | 36
28 | 0.4 | 84 | 33.6 | 7 | 7.46 | 25.8435 | Yes | 36
29 | 0.4 | 84 | 33.6 | 7 | 7.45 | 25.7514 | Yes | 36
30 | 0.4 | 84 | 33.6 | 7 | 7.43 | 25.5682 | Yes | 36
31 | 0.4 | 84 | 33.6 | 7 | 7.41 | 25.3865 | Yes | 36
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised October 2013
PAGE 2 of 2