## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Linn
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2021-02-01
System Name: | Big Lake Youth Camp |  |  | ID#: 41 | 90958 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 25 | 5 | 20 | 30 | 0.15 | 0.15
2 | 25 | 5 | 20 | 30 | 0.13 | 0.13
3 | 25 | 5 | 20 | 30 | 0.14 | 0.14
4 | 25 | 5 | 20 | 30 | 0.12 | 0.12
5 | 25 | 8 | 17 | 30 | 0.11 | 0.11
6 | 25 | 8 | 17 | 30 | 0.13 | 0.13
7 | 25 | 10 | 15 | 30 | 0.14 | 0.14
8 | 25 | 10 | 15 | 30 | 0.15 | 0.15
9 | 25 | 10 | 15 | 30 | 0.17 | 0.17
10 | 25 | 10 | 15 | 30 | 0.18 | 0.18
11 | 25 | 10 | 15 | 30 | 0.16 | 0.16
12 | 25 | 10 | 15 | 30 | 0.14 | 0.14
13 | 25 | 10 | 15 | 30 | 0.15 | 0.15
14 | 25 | 10 | 15 | 30 | 0.12 | 0.12
15 | 25 | 10 | 15 | 30 | 0.11 | 0.11
16 | 25 | 10 | 15 | 30 | 0.14 | 0.14
17 | 25 | 10 | 15 | 30 | 0.13 | 0.13
18 | 25 | 10 | 15 | 30 | 0.11 | 0.11
19 | 25 | 12 | 13 | 30 | 0.12 | 0.12
20 | 25 | 12 | 13 | 30 | 0.14 | 0.14
21 | 25 | 12 | 13 | 30 | 0.16 | 0.16
22 | 25 | 12 | 13 | 30 | 0.15 | 0.15
23 | 25 | 12 | 13 | 30 | 0.13 | 0.13
24 | 25 | 12 | 13 | 30 | 0.12 | 0.12
25 | 25 | 12 | 13 | 30 | 0.11 | 0.11
26 | 25 | 12 | 13 | 30 | 0.14 | 0.14
27 | 25 | 12 | 13 | 30 | 0.13 | 0.13
28 | 25 | 14 | 11 | 30 | 0.16 | 0.16
29 |  |  |  | 30
30 |  |  |  | 30
31 |  |  |  | 30
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME:Ross von Pohle
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE:Ross von Pohle |  | DATE:03/10/2021
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: (503)850-8376 |  | CERT #:N/A
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Big Lake Youth Camp |  | ID#: 41 | 90958 | Month/Year: |  | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.4 | 84 | 33.6 | 7 | 7.41 | 25.3865 | Yes | 36
2 | 0.4 | 84 | 33.6 | 7 | 7.42 | 25.4772 | Yes | 36
3 | 0.4 | 84 | 33.6 | 7 | 7.44 | 25.6596 | Yes | 36
4 | 0.4 | 84 | 33.6 | 7 | 7.43 | 25.5682 | Yes | 36
5 | 0.4 | 84 | 33.6 | 7 | 7.41 | 25.3865 | Yes | 36
6 | 0.4 | 84 | 33.6 | 7 | 7.4 | 25.2962 | Yes | 36
7 | 0.4 | 84 | 33.6 | 7 | 7.43 | 25.5682 | Yes | 36
8 | 0.4 | 84 | 33.6 | 7 | 7.41 | 25.3865 | Yes | 36
9 | 0.4 | 84 | 33.6 | 7 | 7.45 | 25.7514 | Yes | 36
10 | 0.4 | 84 | 33.6 | 6.8 | 7.44 | 26.0058 | Yes | 36
11 | 0.4 | 84 | 33.6 | 6.8 | 7.42 | 25.8207 | Yes | 36
12 | 0.4 | 84 | 33.6 | 6.8 | 7.41 | 25.7287 | Yes | 36
13 | 0.4 | 84 | 33.6 | 6.8 | 7.4 | 25.637 | Yes | 36
14 | 0.4 | 84 | 33.6 | 6.8 | 7.44 | 26.0058 | Yes | 36
15 | 0.4 | 84 | 33.6 | 6.8 | 7.43 | 25.9131 | Yes | 36
16 | 0.4 | 84 | 33.6 | 8.6 | 7.45 | 23.1462 | Yes | 36
17 | 0.4 | 84 | 33.6 | 6.6 | 7.41 | 26.0759 | Yes | 36
18 | 0.4 | 84 | 33.6 | 6.6 | 7.43 | 26.2631 | Yes | 36
19 | 0.4 | 84 | 33.6 | 6.6 | 7.4 | 25.9829 | Yes | 36
20 | 0.4 | 84 | 33.6 | 6.6 | 7.45 | 26.4516 | Yes | 36
21 | 0.5 | 84 | 42 | 6.6 | 7.44 | 26.662 | Yes | 36
22 | 0.5 | 84 | 42 | 6.6 | 7.41 | 26.3773 | Yes | 36
23 | 0.5 | 84 | 42 | 6.6 | 7.43 | 26.5667 | Yes | 36
24 | 0.5 | 84 | 42 | 6.6 | 7.45 | 26.7577 | Yes | 36
25 | 0.5 | 84 | 42 | 6.6 | 7.44 | 26.662 | Yes | 36
26 | 0.5 | 84 | 42 | 6.6 | 7.41 | 26.3773 | Yes | 36
27 | 0.5 | 84 | 42 | 6.6 | 7.43 | 26.5667 | Yes | 36
28 | 0.5 | 84 | 42 | 6.6 | 7.4 | 26.2831 | Yes | 36
29 |  | 84 | [5 empty] | 36
30 |  | 84 | [5 empty] | 36
31 |  | 84 | [5 empty] | 36
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised October 2013
PAGE 2 of 2