## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Linn
Cartridge or Bag Filtration | [5 empty] | Month/Year:
System Name: | Big Lake Youth Camp |  |  | ID#: 41 | 90958 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 40 | 20 | 20 | 30 | 0.11 | 0.11
2 | 45 | 20 | 25 | 30 | 0.13 | 0.13
3 | 50 | 20 | 30 | 30 | 0.1 | 0.1
4 | 20 | 18 | 2 | 30 | 0.15 | 0.15
5 | 20 | 18 | 2 | 30 | 0.14 | 0.14
6 | 20 | 18 | 2 | 30 | 0.12 | 0.12
7 | 20 | 18 | 2 | 30 | 0.13 | 0.13
8 | 20 | 18 | 2 | 30 | 0.16 | 0.16
9 | 20 | 18 | 2 | 30 | 0.14 | 0.14
10 | 20 | 18 | 2 | 30 | 0.13 | 0.13
11 | 20 | 18 | 2 | 30 | 0.15 | 0.15
12 | 20 | 18 | 2 | 30 | 0.16 | 0.16
13 | 20 | 18 | 2 | 30 | 0.14 | 0.14
14 | 20 | 18 | 2 | 30 | 0.13 | 0.13
15 | 20 | 18 | 2 | 30 | 0.15 | 0.15
16 | 20 | 18 | 2 | 30 | 0.17 | 0.17
17 | 20 | 18 | 2 | 30 | 0.18 | 0.18
18 | 20 | 18 | 2 | 30 | 0.17 | 0.17
19 | 20 | 18 | 2 | 30 | 0.16 | 0.16
20 | 20 | 18 | 2 | 30 | 0.14 | 0.14
21 | 20 | 18 | 2 | 30 | 0.16 | 0.16
22 | 20 | 18 | 2 | 30 | 0.17 | 0.17
23 | 20 | 18 | 2 | 30 | 0.18 | 0.18
24 | 20 | 18 | 2 | 30 | 0.19 | 0.19
25 | 20 | 18 | 2 | 30 | 0.17 | 0.17
26 | 20 | 18 | 2 | 30 | 0.15 | 0.15
27 | 20 | 18 | 2 | 30 | 0.16 | 0.16
28 | 20 | 18 | 2 | 30 | 0.17 | 0.17
29 | 20 | 18 | 2 | 30 | 0.15 | 0.15
30 | 20 | 18 | 2 | 30 | 0.16 | 0.16
31 | 20 | 18 | 2 | 30 | 0.17 | 0.17
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME:Ross von Pohle
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | DATE:6/10/2021
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: (503)850-3576 |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Big Lake Youth Camp |  | ID#: 41 | 90958 | Month/Year: |  | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.3 | 84 | 25.2 | 7.2 | 7.35 | 24.242 | Yes | 36
2 | 0.3 | 84 | 25.2 | 7.2 | 7.38 | 24.5017 | Yes | 36
3 | 0.3 | 84 | 25.2 | 7.37 | 7.37 | 24.1398 | Yes | 36
4 | 0.3 | 84 | 25.2 | 7.4 | 7.4 | 24.3496 | Yes | 36
5 | 0.3 | 84 | 25.2 | 7.4 | 7.43 | 24.6105 | Yes | 36
6 | 0.3 | 84 | 25.2 | 7.5 | 7.413 | 24.2998 | Yes | 36
7 | 0.3 | 84 | 25.2 | 7.7 | 7.44 | 24.2091 | Yes | 36
8 | 0.3 | 84 | 25.2 | 7.7 | 7.43 | 24.1233 | Yes | 36
9 | 0.3 | 84 | 25.2 | 7.9 | 7.47 | 24.1444 | Yes | 36
10 | 0.3 | 84 | 25.2 | 7.9 | 7.5 | 24.403 | Yes | 36
11 | 0.3 | 84 | 25.2 | 8.1 | 7.49 | 23.9947 | Yes | 36
12 | 0.3 | 84 | 25.2 | 8.1 | 7.53 | 24.3378 | Yes | 36
13 | 0.3 | 84 | 25.2 | 8.1 | 7.51 | 24.1656 | Yes | 36
14 | 0.3 | 84 | 25.2 | 8.6 | 7.52 | 23.4583 | Yes | 36
15 | 0.3 | 84 | 25.2 | 8.6 | 7.54 | 23.6249 | Yes | 36
16 | 0.3 | 84 | 25.2 | 8.6 | 7.58 | 23.9622 | Yes | 36
17 | 0.3 | 84 | 25.2 | 9.2 | 7.56 | 22.8641 | Yes | 36
18 | 0.3 | 84 | 25.2 | 9.2 | 7.6 | 23.1894 | Yes | 36
19 | 0.3 | 84 | 25.2 | 9.4 | 7.62 | 23.0462 | Yes | 36
20 | 0.3 | 84 | 25.2 | 9.4 | 7.61 | 22.9649 | Yes | 36
21 | 0.3 | 84 | 25.2 | 9.4 | 7.65 | 23.2918 | Yes | 36
22 | 0.3 | 84 | 25.2 | 9.8 | 7.67 | 22.8431 | Yes | 36
23 | 0.3 | 84 | 25.2 | 10.2 | 7.66 | 22.1686 | Yes | 36
24 | 0.3 | 84 | 25.2 | 10.2 | 7.72 | 22.642 | Yes | 36
25 | 0.3 | 84 | 25.2 | 10.2 | 7.68 | 22.3252 | Yes | 36
26 | 0.3 | 84 | 25.2 | 10.9 | 7.7 | 21.4685 | Yes | 36
27 | 0.3 | 84 | 25.2 | 10.9 | 7.76 | 21.9255 | Yes | 36
28 | 0.3 | 84 | 25.2 | 10.9 | 7.8 | 22.2361 | Yes | 36
29 | 0.3 | 84 | 25.2 | 10.9 | 7.83 | 22.4722 | Yes | 36
30 | 0.3 | 84 | 25.2 | 10.9 | 7.85 | 22.6312 | Yes | 36
31 | 0.3 | 84 | 25.2 | 11 | 7.86 | 22.5613 | Yes | 36
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised October 2013
PAGE 2 of 2