## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Linn
Cartridge or Bag Filtration | [5 empty] | Month/Year:
System Name: | Big Lake Youth Camp |  |  | ID#: 41 | 90958 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 20 | 18 | 2 | 30 | 0.16 | 0.16
2 | 20 | 18 | 2 | 30 | 0.15 | 0.15
3 | 20 | 18 | 2 | 30 | 0.14 | 0.14
4 | 20 | 18 | 2 | 30 | 0.16 | 0.16
5 | 20 | 18 | 2 | 30 | 0.15 | 0.15
6 | 20 | 18 | 2 | 30 | 0.17 | 0.17
7 | 20 | 18 | 2 | 30 | 0.18 | 0.18
8 | 20 | 18 | 2 | 30 | 0.16 | 0.16
9 | 20 | 18 | 2 | 30 | 0.17 | 0.17
10 | 20 | 18 | 2 | 30 | 0.16 | 0.16
11 | 20 | 18 | 2 | 30 | 0.17 | 0.17
12 | 20 | 18 | 2 | 30 | 0.18 | 0.18
13 | 20 | 18 | 2 | 30 | 0.19 | 0.19
14 | 20 | 18 | 2 | 30 | 0.17 | 0.17
15 | 20 | 18 | 2 | 30 | 0.15 | 0.15
16 | 20 | 18 | 2 | 30 | 0.18 | 0.18
17 | 20 | 18 | 2 | 30 | 0.2 | 0.2
18 | 20 | 18 | 2 | 30 | 0.19 | 0.19
19 | 18 | 18 | 0 | 30 | 0.17 | 0.17
20 | 18 | 18 | 0 | 30 | 0.16 | 0.16
21 | 18 | 18 | 0 | 30 | 0.19 | 0.19
22 | 18 | 18 | 0 | 30 | 0.2 | 0.2
23 | 18 | 18 | 0 | 30 | 0.18 | 0.18
24 | 15 | 18 | -3 | 30 | 0.17 | 0.17
25 | 15 | 18 | -3 | 30 | 0.19 | 0.19
26 | 15 | 18 | -3 | 30 | 0.2 | 0.2
27 | 12 | 16 | -4 | 30 | 0.17 | 0.17
28 | 12 | 16 | -4 | 30 | 0.19 | 0.19
29 | 12 | 16 | -4 | 30 | 0.18 | 0.18
30 | 8 | 12 | -4 | 30 | 0.2 | 0.2
31 |  |  |  | 30
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME:Ross von Pohle
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE:Ross von Pohle |  | DATE:07/10/2021
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: (503)850-3576 |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Big Lake Youth Camp |  | ID#: 41 | 90958 | Month/Year: |  | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.3 | 84 | 25.2 | 11 | 7.85 | 22.482 | Yes | 36
2 | 0.3 | 84 | 25.2 | 11 | 7.84 | 22.4029 | Yes | 36
3 | 0.3 | 84 | 25.2 | 11 | 7.86 | 22.5613 | Yes | 36
4 | 0.3 | 84 | 25.2 | 11.1 | 7.85 | 22.3339 | Yes | 36
5 | 0.3 | 84 | 25.2 | 11.1 | 7.87 | 22.4918 | Yes | 36
6 | 0.3 | 84 | 25.2 | 11.3 | 7.86 | 22.1185 | Yes | 36
7 | 0.3 | 84 | 25.2 | 11.4 | 7.85 | 21.896 | Yes | 36
8 | 0.3 | 84 | 25.2 | 11.4 | 7.86 | 21.9731 | Yes | 36
9 | 0.3 | 84 | 25.2 | 11.5 | 7.87 | 21.9055 | Yes | 36
10 | 0.3 | 84 | 25.2 | 11.5 | 7.88 | 21.9826 | Yes | 36
11 | 0.3 | 84 | 25.2 | 11.7 | 7.89 | 21.771 | Yes | 36
12 | 0.5 | 84 | 42 | 12 | 7.92 | 22.0634 | Yes | 36
13 | 0.5 | 84 | 42 | 12.5 | 7.95 | 21.5893 | Yes | 36
14 | 0.5 | 84 | 42 | 12.7 | 7.93 | 21.149 | Yes | 36
15 | 0.5 | 84 | 42 | 12.9 | 7.98 | 21.2581 | Yes | 36
16 | 0.5 | 84 | 42 | 13.6 | 8 | 20.4444 | Yes | 36
17 | 0.5 | 84 | 42 | 14 | 7.97 | 19.6904 | Yes | 36
18 | 0.5 | 84 | 42 | 14.7 | 8 | 19.0055 | Yes | 36
19 | 0.6 | 84 | 50.4 | 15 | 7.99 | 18.7738 | Yes | 36
20 | 0.6 | 84 | 50.4 | 15.4 | 8.01 | 18.4169 | Yes | 36
21 | 0.6 | 84 | 50.4 | 15.9 | 8.04 | 18.0133 | Yes | 36
22 | 0.6 | 84 | 50.4 | 16.3 | 8.08 | 17.8016 | Yes | 36
23 | 0.6 | 84 | 50.4 | 16.8 | 8.09 | 17.2831 | Yes | 36
24 | 0.6 | 84 | 50.4 | 17.4 | 8.1 | 16.6679 | Yes | 36
25 | 0.7 | 84 | 58.8 | 17.9 | 8.15 | 16.6108 | Yes | 36
26 | 0.7 | 84 | 58.8 | 18.2 | 8.14 | 16.222 | Yes | 36
27 | 0.7 | 84 | 58.8 | 18.6 | 8.17 | 15.9716 | Yes | 36
28 | 0.7 | 84 | 58.8 | 19 | 8.2 | 15.725 | Yes | 36
29 | 0.7 | 84 | 58.8 | 19.8 | 8.21 | 14.9629 | Yes | 36
30 | 0.8 | 84 | 67.2 | 20.2 | 8.24 | 14.9005 | Yes | 36
31 |  | 84 | [5 empty] | 36
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised October 2013
PAGE 2 of 2