## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Linn
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2021-08-01
System Name: | Big Lake Youth Camp |  |  | ID#: 41 | 90958 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 8 | 6 | 2 | 30 | 0.2 | 0.2
2 | 8 | 6 | 2 | 30 | 0.21 | 0.21
3 | 8 | 6 | 2 | 30 | 0.19 | 0.19
4 | 8 | 6 | 2 | 30 | 0.17 | 0.17
5 | 8 | 6 | 2 | 30 | 0.2 | 0.2
6 | 8 | 6 | 2 | 30 | 0.18 | 0.18
7 | 8 | 6 | 2 | 30 | 0.16 | 0.16
8 | 8 | 6 | 2 | 30 | 0.2 | 0.2
9 | 8 | 6 | 2 | 30 | 0.17 | 0.17
10 | 8 | 6 | 2 | 30 | 0.16 | 0.16
11 | 8 | 6 | 2 | 30 | 0.18 | 0.18
12 | 8 | 6 | 2 | 30 | 0.2 | 0.2
13 | 8 | 6 | 2 | 30 | 0.16 | 0.16
14 | 8 | 6 | 2 | 30 | 0.17 | 0.17
15 | 8 | 6 | 2 | 30 | 0.15 | 0.15
16 | 8 | 6 | 2 | 30 | 0.18 | 0.18
17 | 8 | 6 | 2 | 30 | 0.19 | 0.19
18 | 8 | 6 | 2 | 30 | 0.2 | 0.2
19 | 8 | 6 | 2 | 30 | 0.21 | 0.21
20 | 8 | 6 | 2 | 30 | 0.18 | 0.18
21 | 8 | 8 | 0 | 30 | 0.16 | 0.16
22 | 8 | 8 | 0 | 30 | 0.17 | 0.17
23 | 8 | 8 | 0 | 30 | 0.18 | 0.18
24 | 8 | 8 | 0 | 30 | 0.2 | 0.2
25 | 8 | 8 | 0 | 30 | 0.19 | 0.19
26 | 8 | 8 | 0 | 30 | 0.18 | 0.18
27 | 8 | 8 | 0 | 30 | 0.19 | 0.19
28 | 8 | 8 | 0 | 30 | 0.2 | 0.2
29 | 8 | 8 | 0 | 30 | 0.17 | 0.17
30 | 8 | 8 | 0 | 30 | 0.18 | 0.18
31 | 8 | 8 | 0 | 30 | 0.17 | 0.17
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes / No | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes / No | Yes / No | Yes / No
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME:
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | DATE:
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: ( ) |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Big Lake Youth Camp |  | ID#: 41 | 90958 | Month/Year: | 2021-08-01 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.7 | 84 | 58.8 | 20.4 | 8 | 13.2957 | Yes | 36
2 | 0.7 | 84 | 58.8 | 20.4 | 7.97 | 13.1481 | Yes | 36
3 | 0.6 | 84 | 50.4 | 20.4 | 7.95 | 12.902 | Yes | 36
4 | 0.6 | 84 | 50.4 | 20.4 | 7.98 | 13.047 | Yes | 36
5 | 0.6 | 84 | 50.4 | 20 | 7.96 | 13.302 | Yes | 36
6 | 0.6 | 84 | 50.4 | 20 | 7.99 | 13.4513 | Yes | 36
7 | 0.6 | 84 | 50.4 | 20 | 8 | 13.5014 | Yes | 36
8 | 0.5 | 84 | 42 | 20 | 8.01 | 13.3976 | Yes | 36
9 | 0.5 | 84 | 42 | 19.6 | 7.97 | 13.5582 | Yes | 36
10 | 0.5 | 84 | 42 | 19.6 | 7.94 | 13.4077 | Yes | 36
11 | 0.5 | 84 | 42 | 19.6 | 7.95 | 13.4577 | Yes | 36
12 | 0.5 | 84 | 42 | 19.6 | 7.98 | 13.6087 | Yes | 36
13 | 0.5 | 84 | 42 | 19.3 | 7.98 | 13.8847 | Yes | 36
14 | 0.5 | 84 | 42 | 19.3 | 7.96 | 13.7819 | Yes | 36
15 | 0.5 | 84 | 42 | 19.3 | 7.99 | 13.9364 | Yes | 36
16 | 0.5 | 84 | 42 | 18.9 | 8 | 14.3675 | Yes | 36
17 | 0.5 | 84 | 42 | 18.9 | 7.96 | 14.1556 | Yes | 36
18 | 0.5 | 84 | 42 | 18.9 | 7.97 | 14.2083 | Yes | 36
19 | 0.4 | 84 | 33.6 | 18.2 | 7.95 | 14.611 | Yes | 36
20 | 0.4 | 84 | 33.6 | 18.2 | 7.98 | 14.7746 | Yes | 36
21 | 0.4 | 84 | 33.6 | 18.2 | 7.97 | 14.7199 | Yes | 36
22 | 0.4 | 84 | 33.6 | 18.2 | 7.99 | 14.8295 | Yes | 36
23 | 0.4 | 84 | 33.6 | 17.7 | 7.95 | 15.1072 | Yes | 36
24 | 0.4 | 84 | 33.6 | 17.7 | 7.97 | 15.2196 | Yes | 36
25 | 0.4 | 84 | 33.6 | 17.7 | 7.94 | 15.0513 | Yes | 36
26 | 0.4 | 84 | 33.6 | 17.7 | 7.97 | 15.2196 | Yes | 36
27 | 0.4 | 84 | 33.6 | 17.7 | 7.98 | 15.2761 | Yes | 36
28 | 0.4 | 84 | 33.6 | 17.2 | 8 | 15.9116 | Yes | 36
29 | 0.4 | 84 | 33.6 | 17.2 | 7.99 | 15.8528 | Yes | 36
30 | 0.4 | 84 | 33.6 | 17.2 | 7.97 | 15.7358 | Yes | 36
31 | 0.4 | 84 | 33.6 | 17.2 | 7.98 | 15.7942 | Yes | 36
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised October 2013
PAGE 2 of 2