## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Linn
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2021-09-01
System Name: | Big Lake Youth Camp |  |  | ID#: 41 | 90958 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 8 | 8 | 0 | 30 | 0.17 | 0.17
2 | 8 | 8 | 0 | 30 | 0.16 | 0.16
3 | 8 | 8 | 0 | 30 | 0.18 | 0.18
4 | 8 | 8 | 0 | 30 | 0.15 | 0.15
5 | 8 | 8 | 0 | 30 | 0.14 | 0.14
6 | 8 | 8 | 0 | 30 | 0.16 | 0.16
7 | 8 | 8 | 0 | 30 | 0.14 | 0.14
8 | 8 | 8 | 0 | 30 | 0.13 | 0.13
9 | 8 | 8 | 0 | 30 | 0.11 | 0.11
10 | 8 | 8 | 0 | 30 | 0.13 | 0.13
11 | 8 | 8 | 0 | 30 | 0.14 | 0.14
12 | 8 | 8 | 0 | 30 | 0.16 | 0.16
13 | 8 | 8 | 0 | 30 | 0.14 | 0.14
14 | 8 | 8 | 0 | 30 | 0.12 | 0.12
15 | 9 | 8 | 1 | 30 | 0.11 | 0.11
16 | 9 | 8 | 1 | 30 | 0.1 | 0.1
17 | 9 | 8 | 1 | 30 | 0.14 | 0.14
18 | 910 | 8 | 902 | 30 | 0.13 | 0.13
19 | 10 | 8 | 2 | 30 | 0.15 | 0.15
20 | 10 | 8 | 2 | 30 | 0.17 | 0.17
21 | 12 | 8 | 4 | 30 | 0.15 | 0.15
22 | 14 | 8 | 6 | 30 | 0.13 | 0.13
23 | 14 | 8 | 6 | 30 | 0.14 | 0.14
24 | 16 | 8 | 8 | 30 | 0.12 | 0.12
25 | 16 | 8 | 8 | 30 | 0.17 | 0.17
26 | 17 | 8 | 9 | 30 | 0.15 | 0.15
27 | 18 | 8 | 10 | 30 | 0.13 | 0.13
28 | 18 | 8 | 10 | 30 | 0.16 | 0.16
29 | 20 | 8 | 12 | 30 | 0.13 | 0.13
30 | 20 | 8 | 12 | 30 | 0.12 | 0.12
31 |  |  |  | 30
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME:Ross von Pohle
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | DATE:10/10/2021
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: (503)850-3576 |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Big Lake Youth Camp |  | ID#: 41 | 90958 | Month/Year: | 2021-09-01 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.4 | 84 | 33.6 | 17.2 | 7.98 | 15.7942 | Yes | 36
2 | 0.4 | 84 | 33.6 | 17 | 7.96 | 15.8881 | Yes | 36
3 | 0.4 | 84 | 33.6 | 16.7 | 7.99 | 16.39 | Yes | 36
4 | 0.4 | 84 | 33.6 | 16.3 | 8 | 16.8948 | Yes | 36
5 | 0.4 | 84 | 33.6 | 16 | 7.97 | 17.0455 | Yes | 36
6 | 0.4 | 84 | 33.6 | 15.8 | 7.99 | 17.402 | Yes | 36
7 | 0.4 | 84 | 33.6 | 15.4 | 8 | 17.9372 | Yes | 36
8 | 0.4 | 84 | 33.6 | 15.2 | 7.98 | 18.0436 | Yes | 36
9 | 0.4 | 84 | 33.6 | 14.9 | 7.97 | 18.3391 | Yes | 36
10 | 0.3 | 84 | 25.2 | 14.5 | 8 | 18.8277 | Yes | 36
11 | 0.3 | 84 | 25.2 | 14.5 | 8 | 18.8277 | Yes | 36
12 | 0.3 | 84 | 25.2 | 14.3 | 8 | 19.0794 | Yes | 36
13 | 0.3 | 84 | 25.2 | 14.1 | 7.99 | 19.2633 | Yes | 36
14 | 0.4 | 84 | 33.6 | 13.9 | 7.97 | 19.5982 | Yes | 36
15 | 0.4 | 84 | 33.6 | 13.9 | 7.98 | 19.6705 | Yes | 36
16 | 0.4 | 84 | 33.6 | 13.7 | 7.96 | 19.7869 | Yes | 36
17 | 0.4 | 84 | 33.6 | 13.5 | 7.99 | 20.2739 | Yes | 36
18 | 0.4 | 84 | 33.6 | 13.2 | 8 | 20.7575 | Yes | 36
19 | 0.4 | 84 | 33.6 | 13 | 8.01 | 21.1119 | Yes | 36
20 | 0.4 | 84 | 33.6 | 12.9 | 8 | 21.1742 | Yes | 36
21 | 0.4 | 84 | 33.6 | 12.7 | 7.99 | 21.3778 | Yes | 36
22 | 0.4 | 84 | 33.6 | 12.5 | 7.98 | 21.5834 | Yes | 36
23 | 0.4 | 84 | 33.6 | 12.3 | 7.97 | 21.7675 | Yes | 36
24 | 0.4 | 84 | 33.6 | 12.2 | 7.99 | 22.066 | Yes | 36
25 | 0.4 | 84 | 33.6 | 12 | 7.95 | 22.0469 | Yes | 36
26 | 0.4 | 84 | 33.6 | 11.9 | 7.98 | 22.4285 | Yes | 36
27 | 0.4 | 84 | 33.6 | 11.9 | 7.97 | 22.3496 | Yes | 36
28 | 0.4 | 84 | 33.6 | 11.6 | 7.96 | 22.7173 | Yes | 36
29 | 0.4 | 84 | 33.6 | 11.4 | 7.99 | 23.2656 | Yes | 36
30 | 0.4 | 84 | 33.6 | 11.1 | 8 | 23.818 | Yes | 36
31 |  | 84 | [5 empty] | 36
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised October 2013
PAGE 2 of 2