## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Linn
Cartridge or Bag Filtration | [5 empty] | Month/Year:
System Name: | Big Lake Youth Camp |  |  | ID#: 41 | 90958 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 20 | 8 | 12 | 30 | 0.12 | 0.12
2 | 20 | 8 | 12 | 30 | 0.11 | 0.11
3 | 22 | 8 | 14 | 30 | 0.14 | 0.14
4 | 22 | 8 | 14 | 30 | 0.12 | 0.12
5 | 24 | 8 | 16 | 30 | 0.1 | 0.1
6 | 26 | 8 | 18 | 30 | 0.12 | 0.12
7 | 26 | 8 | 18 | 30 | 0.11 | 0.11
8 | 28 | 8 | 20 | 30 | 0.14 | 0.14
9 | 30 | 7 | 23 | 30 | 0.12 | 0.12
10 | 32 | 7 | 25 | 30 | 0.13 | 0.13
11 | 35 | 7 | 28 | 30 | 0.15 | 0.15
12 | 35 | 7 | 28 | 30 | 0.14 | 0.14
13 | 35 | 7 | 28 | 30 | 0.15 | 0.15
14 | 35 | 7 | 28 | 30 | 0.13 | 0.13
15 | 35 | 7 | 28 | 30 | 0.16 | 0.16
16 | 35 | 7 | 28 | 30 | 0.14 | 0.14
17 | 35 | 7 | 28 | 30 | 0.13 | 0.13
18 | 35 | 7 | 28 | 30 | 0.15 | 0.15
19 | 37 | 7 | 30 | 30 | 0.13 | 0.13
20 | 5 | 5 | 0 | 30 | 0.12 | 0.12
21 | 5 | 6 | -1 | 30 | 0.16 | 0.16
22 | 5 | 6 | -1 | 30 | 0.17 | 0.17
23 | 5 | 6 | -1 | 30 | 0.18 | 0.18
24 | 5 | 7 | -2 | 30 | 0.15 | 0.15
25 | 5 | 7 | -2 | 30 | 0.16 | 0.16
26 | 5 | 7 | -2 | 30 | 0.14 | 0.14
27 | 5 | 8 | -3 | 30 | 0.15 | 0.15
28 | 5 | 8 | -3 | 30 | 0.13 | 0.13
29 | 5 | 8 | -3 | 30 | 0.15 | 0.15
30 | 5 | 9 | -4 | 30 | 0.16 | 0.16
31 | 5 | 9 | -4 | 30 | 0.17 | 0.17
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | YES | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | YES | YES | YES
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Ross von Pohle
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: Ross von Pohle |  | DATE:11/10/2021
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: (503)850-3576 |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Big Lake Youth Camp |  | ID#: 41 | 90958 | Month/Year: |  | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.4 | 84 | 33.6 | 11.1 | 8 | 23.818 | Yes | 36
2 | 0.4 | 84 | 33.6 | 11 | 8.05 | 24.4063 | Yes | 36
3 | 0.4 | 84 | 33.6 | 11 | 8.09 | 24.7558 | Yes | 36
4 | 0.4 | 84 | 33.6 | 11 | 8.1 | 24.8441 | Yes | 36
5 | 0.4 | 84 | 33.6 | 11 | 8.07 | 24.5804 | Yes | 36
6 | 0.4 | 84 | 33.6 | 11 | 8.09 | 24.7558 | Yes | 36
7 | 0.4 | 84 | 33.6 | 10.9 | 8.04 | 24.4825 | Yes | 36
8 | 0.4 | 84 | 33.6 | 10.9 | 8.05 | 24.5696 | Yes | 36
9 | 0.4 | 84 | 33.6 | 10.9 | 8.01 | 24.223 | Yes | 36
10 | 0.4 | 84 | 33.6 | 10.8 | 8.03 | 24.5588 | Yes | 36
11 | 0.4 | 84 | 33.6 | 10.8 | 8.07 | 24.9107 | Yes | 36
12 | 0.4 | 84 | 33.6 | 10.6 | 8.04 | 24.9776 | Yes | 36
13 | 0.4 | 84 | 33.6 | 10.6 | 8.03 | 24.8889 | Yes | 36
14 | 0.4 | 84 | 33.6 | 10.2 | 8.05 | 25.7467 | Yes | 36
15 | 0.4 | 84 | 33.6 | 10.2 | 8.07 | 25.9312 | Yes | 36
16 | 0.4 | 84 | 33.6 | 10.2 | 8.06 | 25.8388 | Yes | 36
17 | 0.4 | 84 | 33.6 | 9.9 | 8.1 | 26.7441 | Yes | 36
18 | 0.4 | 84 | 33.6 | 9.9 | 8.07 | 26.4584 | Yes | 36
19 | 0.5 | 84 | 42 | 9.6 | 8.08 | 27.4085 | Yes | 36
20 | 0.5 | 84 | 42 | 9.6 | 8.09 | 27.507 | Yes | 36
21 | 0.5 | 84 | 42 | 9.3 | 8.06 | 27.7681 | Yes | 36
22 | 0.5 | 84 | 42 | 9.3 | 8.1 | 28.1703 | Yes | 36
23 | 0.5 | 84 | 42 | 9.3 | 8.07 | 27.8681 | Yes | 36
24 | 0.6 | 84 | 50.4 | 8.9 | 8.03 | 28.55 | Yes | 36
25 | 0.6 | 84 | 50.4 | 8.8 | 8.01 | 28.5373 | Yes | 36
26 | 0.6 | 84 | 50.4 | 8.5 | 8.04 | 29.4392 | Yes | 36
27 | 0.6 | 84 | 50.4 | 8.2 | 8.02 | 29.8277 | Yes | 36
28 | 0.7 | 84 | 58.8 | 8 | 8.05 | 30.9231 | Yes | 36
29 | 0.7 | 84 | 58.8 | 7.8 | 8.06 | 31.4606 | Yes | 36
30 | 0.7 | 84 | 58.8 | 7.6 | 8.03 | 31.5467 | Yes | 36
31 | 0.7 | 84 | 58.8 | 7.6 | 8.01 | 31.3187 | Yes | 36
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised October 2013
PAGE 2 of 2