## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Linn
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2021-11-01
System Name: | Big Lake Youth Camp |  |  | ID#: 41 | 90958 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 5 | 9 | -4 | 30 | 0.17 | 0.17
2 | 5 | 9 | -4 | 30 | 0.16 | 0.16
3 | 5 | 9 | -4 | 30 | 0.15 | 0.15
4 | 5 | 9 | -4 | 30 | 0.14 | 0.14
5 | 5 | 9 | -4 | 30 | 0.11 | 0.11
6 | 5 | 9 | -4 | 30 | 0.13 | 0.13
7 | 5 | 9 | -4 | 30 | 0.15 | 0.15
8 | 5 | 9 | -4 | 30 | 0.14 | 0.14
9 | 5 | 9 | -4 | 30 | 0.18 | 0.18
10 | 5 | 9 | -4 | 30 | 0.16 | 0.16
11 | 5 | 9 | -4 | 30 | 0.14 | 0.14
12 | 5 | 9 | -4 | 30 | 0.13 | 0.13
13 | 5 | 9 | -4 | 30 | 0.17 | 0.17
14 | 5 | 9 | -4 | 30 | 0.18 | 0.18
15 | 5 | 9 | -4 | 30 | 0.14 | 0.14
16 | 5 | 9 | -4 | 30 | 0.15 | 0.15
17 | 10 | 9 | 1 | 30 | 0.13 | 0.13
18 | 10 | 9 | 1 | 30 | 0.16 | 0.16
19 | 10 | 9 | 1 | 30 | 0.14 | 0.14
20 | 10 | 9 | 1 | 30 | 0.15 | 0.15
21 | 10 | 9 | 1 | 30 | 0.12 | 0.12
22 | 15 | 9 | 6 | 30 | 0.14 | 0.14
23 | 15 | 9 | 6 | 30 | 0.17 | 0.17
24 | 15 | 9 | 6 | 30 | 0.18 | 0.18
25 | 15 | 9 | 6 | 30 | 0.13 | 0.13
26 | 15 | 9 | 6 | 30 | 0.15 | 0.15
27 | 18 | 9 | 9 | 30 | 0.14 | 0.14
28 | 20 | 9 | 11 | 30 | 0.13 | 0.13
29 | 20 | 9 | 11 | 30 | 0.15 | 0.15
30 | 25 | 10 | 15 | 30 | 0.18 | 0.18
31 |  |  |  | 30
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME:Ross von Pohle
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE:Ross von Pohle |  | DATE:12/08/2021
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: (503)850-3576 |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Big Lake Youth Camp |  | ID#: 41 | 90958 | Month/Year: | 2021-11-01 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.7 | 84 | 58.8 | 7.6 | 8.01 | 31.3187 | Yes | 36
2 | 0.7 | 84 | 58.8 | 7.6 | 8.05 | 31.7766 | Yes | 36
3 | 0.7 | 84 | 58.8 | 7.6 | 8.03 | 31.5467 | Yes | 36
4 | 0.7 | 84 | 58.8 | 7.6 | 8.07 | 32.0082 | Yes | 36
5 | 0.7 | 84 | 58.8 | 7.6 | 8.06 | 31.8922 | Yes | 36
6 | 0.7 | 84 | 58.8 | 7.6 | 8.09 | 32.2417 | Yes | 36
7 | 0.7 | 84 | 58.8 | 7.6 | 8.11 | 32.4769 | Yes | 36
8 | 0.7 | 84 | 58.8 | 7.6 | 8.15 | 32.953 | Yes | 36
9 | 0.7 | 84 | 58.8 | 7.6 | 8.1 | 32.3591 | Yes | 36
10 | 0.7 | 84 | 58.8 | 7.6 | 8.14 | 32.8333 | Yes | 36
11 | 0.7 | 84 | 58.8 | 7.6 | 8.13 | 32.714 | Yes | 36
12 | 0.7 | 84 | 58.8 | 7.6 | 8.09 | 32.2417 | Yes | 36
13 | 0.7 | 84 | 58.8 | 7.6 | 8.11 | 32.4769 | Yes | 36
14 | 0.7 | 84 | 58.8 | 7.6 | 8.16 | 33.0732 | Yes | 36
15 | 0.7 | 84 | 58.8 | 7.6 | 8.14 | 32.8333 | Yes | 36
16 | 0.7 | 84 | 58.8 | 7.6 | 8.17 | 33.1938 | Yes | 36
17 | 0.7 | 84 | 58.8 | 7.4 | 8.15 | 33.4065 | Yes | 36
18 | 0.7 | 84 | 58.8 | 7.4 | 8.13 | 33.164 | Yes | 36
19 | 0.7 | 84 | 58.8 | 7.4 | 8.16 | 33.5284 | Yes | 36
20 | 0.7 | 84 | 58.8 | 7.4 | 8.14 | 33.285 | Yes | 36
21 | 0.7 | 84 | 58.8 | 7.4 | 8.12 | 33.0435 | Yes | 36
22 | 0.7 | 84 | 58.8 | 7.4 | 8.17 | 33.6508 | Yes | 36
23 | 0.7 | 84 | 58.8 | 7.4 | 8.15 | 33.4065 | Yes | 36
24 | 0.7 | 84 | 58.8 | 7.4 | 8.18 | 33.7737 | Yes | 36
25 | 0.5 | 84 | 42 | 7.4 | 8.12 | 32.2799 | Yes | 36
26 | 0.5 | 84 | 42 | 7.4 | 8.13 | 32.3975 | Yes | 36
27 | 0.5 | 84 | 42 | 7.3 | 8.11 | 32.383 | Yes | 36
28 | 0.5 | 84 | 42 | 7.3 | 8.09 | 32.1484 | Yes | 36
29 | 0.5 | 84 | 42 | 7.3 | 8.1 | 32.2655 | Yes | 36
30 | 0.5 | 84 | 42 | 7.3 | 8.12 | 32.5009 | Yes | 36
31 |  | 84 | [5 empty] | 36
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised October 2013
PAGE 2 of 2