## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Linn
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2022-01-01
System Name: | Big Lake Youth Camp |  |  | ID#: 41 | 90958 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 5 | 4 | 1 | 30 | 0.11 | 0.11
2 | 5 | 4 | 1 | 30 | 0.13 | 0.13
3 | 5 | 4 | 1 | 30 | 0.15 | 0.15
4 | 5 | 4 | 1 | 30 | 0.12 | 0.12
5 | 5 | 4 | 1 | 30 | 0.11 | 0.11
6 | 5 | 4 | 1 | 30 | 0.15 | 0.15
7 | 5 | 4 | 1 | 30 | 0.13 | 0.13
8 | 5 | 4 | 1 | 30 | 0.16 | 0.16
9 | 5 | 4 | 1 | 30 | 0.12 | 0.12
10 | 5 | 4 | 1 | 30 | 0.14 | 0.14
11 | 5 | 4 | 1 | 30 | 0.13 | 0.13
12 | 5 | 4 | 1 | 30 | 0.12 | 0.12
13 | 5 | 4 | 1 | 30 | 0.11 | 0.11
14 | 5 | 4 | 1 | 30 | 0.1 | 0.1
15 | 5 | 4 | 1 | 30 | 0.13 | 0.13
16 | 7 | 4 | 3 | 30 | 0.15 | 0.15
17 | 7 | 4 | 3 | 30 | 0.16 | 0.16
18 | 7 | 4 | 3 | 30 | 0.14 | 0.14
19 | 7 | 4 | 3 | 30 | 0.13 | 0.13
20 | 7 | 4 | 3 | 30 | 0.15 | 0.15
21 | 7 | 4 | 3 | 30 | 0.16 | 0.16
22 | 7 | 4 | 3 | 30 | 0.13 | 0.13
23 | 10 | 4 | 6 | 30 | 0.11 | 0.11
24 | 10 | 4 | 6 | 30 | 0.12 | 0.12
25 | 10 | 4 | 6 | 30 | 0.14 | 0.14
26 | 10 | 4 | 6 | 30 | 0.12 | 0.12
27 | 10 | 4 | 6 | 30 | 0.15 | 0.15
28 | 10 | 4 | 6 | 30 | 0.13 | 0.13
29 | 10 | 4 | 6 | 30 | 0.14 | 0.14
30 | 10 | 4 | 6 | 30 | 0.12 | 0.12
31 | 10 | 4 | 6 | 30 | 0.11 | 0.11
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME:Ross von Pohle
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | DATE:02/10/2022
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: (503)850-3576 |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Big Lake Youth Camp |  | ID#: 41 | 90958 | Month/Year: | 2022-01-01 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.5 | 84 | 42 | 5 | 7.96 | 35.8868 | Yes | 36
2 | 0.5 | 84 | 42 | 5 | 8 | 36.4163 | Yes | 36
3 | 0.5 | 84 | 42 | 5 | 7.97 | 36.0184 | Yes | 36
4 | 0.5 | 84 | 42 | 5 | 8.01 | 36.55 | Yes | 36
5 | 0.5 | 84 | 42 | 5 | 8.04 | 36.9542 | Yes | 36
6 | 0.5 | 84 | 42 | 5 | 7.99 | 36.2832 | Yes | 36
7 | 0.5 | 84 | 42 | 5 | 7.93 | 35.495 | Yes | 36
8 | 0.5 | 84 | 42 | 5 | 8.02 | 36.6842 | yes | 36
9 | 0.5 | 84 | 42 | 5 | 8 | 36.4163 | Ye | 36
10 | 0.5 | 84 | 42 | 5 | 7.96 | 35.8868 | Yes | 36
11 | 0.5 | 84 | 42 | 5 | 8 | 36.4163 | Yes | 36
12 | 0.5 | 84 | 42 | 5 | 7.99 | 36.2832 | Yes | 36
13 | 0.5 | 84 | 42 | 5 | 8 | 36.4163 | Yes | 36
14 | 0.5 | 84 | 42 | 5 | 8.01 | 36.55 | Yes | 36
15 | 0.5 | 84 | 42 | 5 | 8.03 | 36.8189 | Yes | 36
16 | 0.5 | 84 | 42 | 5 | 8.05 | 37.0899 | Yes | 36
17 | 0.5 | 84 | 42 | 5 | 8.08 | 37.5004 | Yes | 36
18 | 0.5 | 84 | 42 | 5 | 8.04 | 36.9542 | Yes | 36
19 | 0.5 | 84 | 42 | 5 | 8.09 | 37.6383 | Yes | 36
20 | 0.5 | 84 | 42 | 5 | 8.1 | 37.7768 | Yes | 36
21 | 0.5 | 84 | 42 | 5 | 8.12 | 38.0553 | Yes | 36
22 | 0.5 | 84 | 42 | 5 | 8.09 | 37.6383 | Yes | 36
23 | 0.5 | 84 | 42 | 5 | 8.07 | 37.3631 | Yes | 36
24 | 0.5 | 84 | 42 | 5 | 8.11 | 37.9158 | Yes | 36
25 | 0.5 | 84 | 42 | 5 | 8.15 | 38.4771 | Yes | 36
26 | 0.5 | 84 | 42 | 5 | 8.12 | 38.0553 | Yes | 36
27 | 0.5 | 84 | 42 | 5 | 8.11 | 37.9158 | Yes | 36
28 | 0.5 | 84 | 42 | 5 | 8.1 | 37.7768 | Yes | 36
29 | 0.5 | 84 | 42 | 5 | 8.07 | 37.3631 | Yes | 36
30 | 0.5 | 84 | 42 | 5 | 8.06 | 37.2262 | Yes | 36
31 | 0.5 | 84 | 42 | 5 | 8.08 | 37.5004 | Yes | 36
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised October 2013
PAGE 2 of 2