## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Linn
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2022-05-01
System Name: | Big Lake Youth Camp |  |  | ID#: 41 | 90958 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 20 | 10 | 10 | 30 | 0.15 | 0.15
2 | 20 | 10 | 10 | 30 | 0.16 | 0.16
3 | 20 | 10 | 10 | 30 | 0.14 | 0.14
4 | 20 | 10 | 10 | 30 | 0.17 | 0.17
5 | 21 | 10 | 11 | 30 | 0.15 | 0.15
6 | 23 | 10 | 13 | 30 | 0.16 | 0.16
7 | 26 | 10 | 16 | 30 | 0.14 | 0.14
8 | 30 | 10 | 20 | 30 | 0.16 | 0.16
9 | 35 | 10 | 25 | 30 | 0.15 | 0.15
10 | 40 | 10 | 30 | 30 | 0.17 | 0.17
11 | 10 | 10 | 0 | 30 | 0.14 | 0.14
12 | 10 | 10 | 0 | 30 | 0.13 | 0.13
13 | 10 | 10 | 0 | 30 | 0.15 | 0.15
14 | 12 | 10 | 2 | 30 | 0.14 | 0.14
15 | 12 | 10 | 2 | 30 | 0.16 | 0.16
16 | 12 | 10 | 2 | 30 | 0.17 | 0.17
17 | 12 | 10 | 2 | 30 | 0.18 | 0.18
18 | 15 | 10 | 5 | 30 | 0.16 | 0.16
19 | 15 | 10 | 5 | 30 | 0.17 | 0.17
20 | 15 | 10 | 5 | 30 | 0.15 | 0.15
21 | 20 | 10 | 10 | 30 | 0.14 | 0.14
22 | 20 | 10 | 10 | 30 | 0.13 | 0.13
23 | 20 | 10 | 10 | 30 | 0.15 | 0.15
24 | 20 | 10 | 10 | 30 | 0.17 | 0.17
25 | 25 | 10 | 15 | 30 | 0.16 | 0.16
26 | 30 | 10 | 20 | 30 | 0.17 | 0.17
27 | 40 | 10 | 30 | 30 | 0.14 | 0.14
28 | 10 | 10 | 0 | 30 | 0.15 | 0.15
29 | 10 | 10 | 0 | 30 | 0.16 | 0.16
30 | 10 | 10 | 0 | 30 | 0.15 | 0.15
31 | 11 | 10 | 1 | 30 | 0.14 | 0.14
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME:Ross von Pohle
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | DATE:06/10/2022
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: (503)850-3576 |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Big Lake Youth Camp |  | ID#: 41 | 90958 | Month/Year: | 2022-05-01 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.5 | 84 | 42 | 4.8 | 7.8 | 34.3158 | Yes | 36
2 | 0.5 | 84 | 42 | 4.8 | 7.77 | 33.9423 | Yes | 36
3 | 0.5 | 84 | 42 | 4.8 | 7.79 | 34.1908 | Yes | 36
4 | 0.5 | 84 | 42 | 4.8 | 7.81 | 34.4413 | Yes | 36
5 | 0.5 | 84 | 42 | 4.8 | 7.83 | 34.6937 | Yes | 36
6 | 0.5 | 84 | 42 | 4.8 | 7.8 | 34.3158 | Yes | 36
7 | 0.5 | 84 | 42 | 4.8 | 7.81 | 34.4413 | Yes | 36
8 | 0.5 | 84 | 42 | 4.8 | 7.79 | 34.1908 | Yes | 36
9 | 0.5 | 84 | 42 | 4.8 | 7.82 | 34.5673 | Yes | 36
10 | 0.5 | 84 | 42 | 4.8 | 7.81 | 34.4413 | Yes | 36
11 | 0.5 | 84 | 42 | 5 | 7.85 | 34.4723 | Yes | 36
12 | 0.5 | 84 | 42 | 5 | 7.88 | 34.8521 | Yes | 36
13 | 0.5 | 84 | 42 | 5 | 7.83 | 34.2216 | Yes | 36
14 | 0.5 | 84 | 42 | 5.1 | 7.86 | 34.3622 | Yes | 36
15 | 0.5 | 84 | 42 | 5.1 | 7.89 | 34.7407 | Yes | 36
16 | 0.5 | 84 | 42 | 5.2 | 7.9 | 34.6296 | Yes | 36
17 | 0.5 | 84 | 42 | 5.4 | 7.88 | 33.9101 | Yes | 36
18 | 0.5 | 84 | 42 | 5.5 | 7.91 | 34.0494 | Yes | 36
19 | 0.5 | 84 | 42 | 5.5 | 7.93 | 34.2988 | Yes | 36
20 | 0.5 | 84 | 42 | 5.6 | 7.9 | 33.6941 | Yes | 36
21 | 0.5 | 84 | 42 | 5.6 | 7.92 | 33.9407 | Yes | 36
22 | 0.5 | 84 | 42 | 5.7 | 7.94 | 33.9559 | Yes | 36
23 | 0.5 | 84 | 42 | 5.7 | 7.95 | 34.08 | Yes | 36
24 | 0.5 | 84 | 42 | 5.7 | 7.94 | 33.9559 | Yes | 36
25 | 0.5 | 84 | 42 | 5.9 | 7.96 | 33.7396 | Yes | 36
26 | 0.4 | 84 | 33.6 | 5.9 | 7.94 | 33.1048 | Yes | 36
27 | 0.4 | 84 | 33.6 | 6.1 | 7.96 | 32.8941 | Yes | 36
28 | 0.4 | 84 | 33.6 | 6.1 | 7.9 | 32.1842 | Yes | 36
29 | 0.4 | 84 | 33.6 | 6.1 | 7.93 | 32.5371 | Yes | 36
30 | 0.4 | 84 | 33.6 | 6.1 | 7.92 | 32.419 | Yes | 36
31 | 0.4 | 84 | 33.6 | 6.1 | 7.95 | 32.7747 | Yes | 36
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised October 2013
PAGE 2 of 2