## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Linn
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2022-09-01
System Name: | Big Lake Youth Camp |  |  | ID#: 41 | 90958 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 20 | 10 | 10 | 30 | 0.1 | 0.1
2 | 20 | 10 | 10 | 30 | 0.12 | 0.12
3 | 20 | 10 | 10 | 30 | 0.11 | 0.11
4 | 20 | 10 | 10 | 30 | 0.13 | 0.13
5 | 20 | 10 | 10 | 30 | 0.14 | 0.14
6 | 25 | 10 | 15 | 30 | 0.12 | 0.12
7 | 25 | 10 | 15 | 30 | 0.13 | 0.13
8 | 25 | 10 | 15 | 30 | 0.15 | 0.15
9 | 30 | 10 | 20 | 30 | 0.13 | 0.13
10 | 30 | 10 | 20 | 30 | 0.11 | 0.11
11 | 30 | 10 | 20 | 30 | 0.1 | 0.1
12 | 30 | 10 | 20 | 30 | 0.14 | 0.14
13 | 30 | 10 | 20 | 30 | 0.15 | 0.15
14 | 35 | 10 | 25 | 30 | 0.13 | 0.13
15 | 35 | 10 | 25 | 30 | 0.14 | 0.14
16 | 35 | 10 | 25 | 30 | 0.12 | 0.12
17 | 35 | 10 | 25 | 30 | 0.15 | 0.15
18 | 35 | 10 | 25 | 30 | 0.12 | 0.12
19 | 35 | 10 | 25 | 30 | 0.14 | 0.14
20 | 35 | 10 | 25 | 30 | 0.15 | 0.15
21 | 40 | 10 | 30 | 30 | 0.14 | 0.14
22 | 10 | 8 | 2 | 30 | 0.12 | 0.12
23 | 10 | 8 | 2 | 30 | 0.14 | 0.14
24 | 10 | 8 | 2 | 30 | 0.13 | 0.13
25 | 10 | 8 | 2 | 30 | 0.12 | 0.12
26 | 10 | 8 | 2 | 30 | 0.11 | 0.11
27 | 10 | 8 | 2 | 30 | 0.13 | 0.13
28 | 10 | 8 | 2 | 30 | 0.15 | 0.15
29 | 10 | 8 | 2 | 30 | 0.12 | 0.12
30 | 10 | 8 | 2 | 30 | 0.14 | 0.14
31 |  |  |  | 30
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME:Ross von Pohle
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | DATE:10/10/2022
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: (503)850-3576 |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Big Lake Youth Camp |  | ID#: 41 | 90958 | Month/Year: | 2022-09-01 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.3 | 84 | 25.2 | 15 | 8.5 | 21.8961 | Yes | 36
2 | 0.3 | 84 | 25.2 | 15 | 8.51 | 21.9768 | Yes | 36
3 | 0.3 | 84 | 25.2 | 15 | 8.52 | 22.0577 | Yes | 36
4 | 0.3 | 84 | 25.2 | 14.8 | 8.5 | 22.1879 | Yes | 36
5 | 0.3 | 84 | 25.2 | 14.8 | 8.53 | 22.434 | Yes | 36
6 | 0.3 | 84 | 25.2 | 14.8 | 8.55 | 22.5995 | Yes | 36
7 | 0.3 | 84 | 25.2 | 14.7 | 8.51 | 22.4176 | Yes | 36
8 | 0.3 | 84 | 25.2 | 14.7 | 8.53 | 22.583 | Yes | 36
9 | 0.3 | 84 | 25.2 | 14.6 | 8.52 | 22.6495 | Yes | 36
10 | 0.3 | 84 | 25.2 | 14.6 | 8.54 | 22.8166 | Yes | 36
11 | 0.3 | 84 | 25.2 | 14.5 | 8.51 | 22.7162 | Yes | 36
12 | 0.3 | 84 | 25.2 | 14.5 | 8.49 | 22.5499 | Yes | 36
13 | 0.3 | 84 | 25.2 | 14.5 | 8.53 | 22.8838 | Yes | 36
14 | 0.3 | 84 | 25.2 | 14.4 | 8.55 | 23.2056 | Yes | 36
15 | 0.3 | 84 | 25.2 | 14.4 | 8.54 | 23.1205 | Yes | 36
16 | 0.3 | 84 | 25.2 | 14.4 | 8.52 | 22.9512 | Yes | 36
17 | 0.3 | 84 | 25.2 | 14.4 | 8.51 | 22.867 | Yes | 36
18 | 0.3 | 84 | 25.2 | 14.3 | 8.5 | 22.9344 | Yes | 36
19 | 0.3 | 84 | 25.2 | 14.2 | 8.53 | 23.3424 | Yes | 36
20 | 0.3 | 84 | 25.2 | 14.2 | 8.52 | 23.2569 | Yes | 36
21 | 0.3 | 84 | 25.2 | 14 | 8.55 | 23.8276 | Yes | 36
22 | 0.3 | 84 | 25.2 | 14 | 8.54 | 23.7402 | Yes | 36
23 | 0.3 | 84 | 25.2 | 14 | 8.55 | 23.8276 | Yes | 36
24 | 0.3 | 84 | 25.2 | 14 | 8.56 | 23.9152 | Yes | 36
25 | 0.3 | 84 | 25.2 | 14 | 8.54 | 23.7402 | Yes | 36
26 | 0.3 | 84 | 25.2 | 14 | 8.52 | 23.5665 | Yes | 36
27 | 0.3 | 84 | 25.2 | 14 | 8.53 | 23.6532 | Yes | 36
28 | 0.3 | 84 | 25.2 | 14 | 8.51 | 23.4801 | Yes | 36
29 | 0.3 | 84 | 25.2 | 14 | 8.5 | 23.394 | Yes | 36
30 | 0.3 | 84 | 25.2 | 14 | 8.53 | 23.6532 | Yes | 36
31 |  | 84 | [5 empty] | 36
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised October 2013
PAGE 2 of 2