## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Linn
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2022-10-01
System Name: | Big Lake Youth Camp |  |  | ID#: 41 | 90958 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 10 | 8 | 2 | 30 | 0.14 | 0.14
2 | 10 | 8 | 2 | 30 | 0.12 | 0.12
3 | 10 | 8 | 2 | 30 | 0.14 | 0.14
4 | 10 | 8 | 2 | 30 | 0.11 | 0.11
5 | 10 | 8 | 2 | 30 | 0.12 | 0.12
6 | 10 | 8 | 2 | 30 | 0.15 | 0.15
7 | 10 | 8 | 2 | 30 | 0.13 | 0.13
8 | 10 | 8 | 2 | 30 | 0.14 | 0.14
9 | 10 | 8 | 2 | 30 | 0.16 | 0.16
10 | 10 | 9 | 1 | 30 | 0.13 | 0.13
11 | 10 | 9 | 1 | 30 | 0.14 | 0.14
12 | 10 | 9 | 1 | 30 | 0.12 | 0.12
13 | 10 | 9 | 1 | 30 | 0.14 | 0.14
14 | 10 | 9 | 1 | 30 | 0.15 | 0.15
15 | 10 | 9 | 1 | 30 | 0.14 | 0.14
16 | 10 | 9 | 1 | 30 | 0.12 | 0.12
17 | 10 | 9 | 1 | 30 | 0.13 | 0.13
18 | 11 | 9 | 2 | 30 | 0.11 | 0.11
19 | 11 | 9 | 2 | 30 | 0.15 | 0.15
20 | 11 | 9 | 2 | 30 | 0.14 | 0.14
21 | 11 | 9 | 2 | 30 | 0.13 | 0.13
22 | 11 | 9 | 2 | 30 | 0.12 | 0.12
23 | 11 | 9 | 2 | 30 | 0.14 | 0.14
24 | 11 | 10 | 1 | 30 | 0.15 | 0.15
25 | 11 | 10 | 1 | 30 | 0.16 | 0.16
26 | 11 | 10 | 1 | 30 | 0.14 | 0.14
27 | 11 | 10 | 1 | 30 | 0.12 | 0.12
28 | 11 | 10 | 1 | 30 | 0.13 | 0.13
29 | 12 | 11 | 1 | 30 | 0.11 | 0.11
30 | 12 | 11 | 1 | 30 | 0.15 | 0.15
31 | 12 | 12 | 0 | 30 | 0.17 | 0.17
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME:Ross von Pohle
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE:Ross von Pohle |  | DATE:11-10-2022
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: (503)850-3576 |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Big Lake Youth Camp |  | ID#: 41 | 90958 | Month/Year: | 2022-10-01 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.3 | 84 | 25.2 | 14 | 8.53 | 23.6532 | Yes | 36
2 | 0.5 | 84 | 42 | 14 | 8.51 | 24.0164 | Yes | 36
3 | 0.5 | 84 | 42 | 14 | 8.54 | 24.2823 | Yes | 36
4 | 0.5 | 84 | 42 | 14 | 8.52 | 24.1047 | Yes | 36
5 | 0.5 | 84 | 42 | 14 | 8.5 | 23.9283 | Yes | 36
6 | 0.5 | 84 | 42 | 14 | 8.51 | 24.0164 | Yes | 36
7 | 0.5 | 84 | 42 | 14 | 8.53 | 24.1933 | Yes | 36
8 | 0.5 | 84 | 42 | 14 | 8.52 | 24.1047 | Yes | 36
9 | 0.5 | 84 | 42 | 14 | 8.51 | 24.0164 | Yes | 36
10 | 0.5 | 84 | 42 | 14 | 8.49 | 23.8406 | Yes | 36
11 | 0.5 | 84 | 42 | 14 | 8.53 | 24.1933 | Yes | 36
12 | 0.5 | 84 | 42 | 14 | 8.52 | 24.1047 | Yes | 36
13 | 0.5 | 84 | 42 | 14 | 8.54 | 24.2823 | Yes | 36
14 | 0.5 | 84 | 42 | 14 | 8.51 | 24.0164 | Yes | 36
15 | 0.5 | 84 | 42 | 14 | 8.51 | 24.0164 | Yes | 36
16 | 0.5 | 84 | 42 | 14 | 8.5 | 23.9283 | Yes | 36
17 | 0.5 | 84 | 42 | 14 | 8.52 | 24.1047 | Yes | 36
18 | 0.5 | 84 | 42 | 14 | 8.54 | 24.2823 | Yes | 36
19 | 0.5 | 84 | 42 | 14 | 8.51 | 24.0164 | Yes | 36
20 | 0.5 | 84 | 42 | 14 | 8.53 | 24.1933 | Yes | 36
21 | 0.5 | 84 | 42 | 14 | 8.52 | 24.1047 | Yes | 36
22 | 0.5 | 84 | 42 | 14 | 8.51 | 24.0164 | Yes | 36
23 | 0.5 | 84 | 42 | 13.8 | 8.54 | 24.6054 | Yes | 36
24 | 0.5 | 84 | 42 | 13.8 | 8.52 | 24.4254 | Yes | 36
25 | 0.5 | 84 | 42 | 13.8 | 8.54 | 24.6054 | Yes | 36
26 | 0.5 | 84 | 42 | 13.4 | 8.53 | 25.1718 | Yes | 36
27 | 0.5 | 84 | 42 | 13.4 | 8.51 | 24.9877 | Yes | 36
28 | 0.5 | 84 | 42 | 13.4 | 8.5 | 24.8962 | Yes | 36
29 | 0.5 | 84 | 42 | 12.9 | 8.51 | 25.8267 | Yes | 36
30 | 0.5 | 84 | 42 | 12.9 | 8.52 | 25.9215 | Yes | 36
31 | 0.5 | 84 | 42 | 12.9 | 8.5 | 25.7321 | Yes | 36
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised October 2013
PAGE 2 of 2