## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Linn
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2022-11-01
System Name: | Big Lake Youth Camp |  |  | ID#: 41 | 90958 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 12 | 12 | 0 | 30 | 0.17 | 0.17
2 | 12 | 12 | 0 | 30 | 0.15 | 0.15
3 | 12 | 12 | 0 | 30 | 0.16 | 0.16
4 | 12 | 12 | 0 | 30 | 0.14 | 0.14
5 | 12 | 12 | 0 | 30 | 0.13 | 0.13
6 | 12 | 12 | 0 | 30 | 0.16 | 0.16
7 | 12 | 12 | 0 | 30 | 0.15 | 0.15
8 | 12 | 12 | 0 | 30 | 0.17 | 0.17
9 | 12 | 12 | 0 | 30 | 0.16 | 0.16
10 | 12 | 10 | 2 | 30 | 0.17 | 0.17
11 | 12 | 10 | 2 | 30 | 0.18 | 0.18
12 | 12 | 10 | 2 | 30 | 0.15 | 0.15
13 | 12 | 10 | 2 | 30 | 0.16 | 0.16
14 | 12 | 10 | 2 | 30 | 0.14 | 0.14
15 | 12 | 10 | 2 | 30 | 0.125 | 0.13
16 | 12 | 10 | 2 | 30 | 0.15 | 0.15
17 | 12 | 10 | 2 | 30 | 0.12 | 0.12
18 | 12 | 10 | 2 | 30 | 0.15 | 0.15
19 | 12 | 10 | 2 | 30 | 0.14 | 0.14
20 | 12 | 10 | 2 | 30 | 0.15 | 0.15
21 | 12 | 10 | 2 | 30 | 0.13 | 0.13
22 | 12 | 10 | 2 | 30 | 0.12 | 0.12
23 | 12 | 10 | 2 | 30 | 0.14 | 0.14
24 | 12 | 10 | 2 | 30 | 0.15 | 0.15
25 | 15 | 12 | 3 | 30 | 0.14 | 0.14
26 | 15 | 12 | 3 | 30 | 0.16 | 0.16
27 | 15 | 12 | 3 | 30 | 0.17 | 0.17
28 | 15 | 12 | 3 | 30 | 0.14 | 0.14
29 | 15 | 12 | 3 | 30 | 0.13 | 0.13
30 | 15 | 12 | 3 | 30 | 0.15 | 0.15
31 |  |  |  | 30
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME:Ross von Pohle
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE:Ross von Pohle |  | DATE:12/10/2022
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: (503)850-3576 |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Big Lake Youth Camp |  | ID#: 41 | 90958 | Month/Year: | 2022-11-01 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.5 | 84 | 42 | 12.1 | 8.5 | 26.9295 | Yes | 36
2 | 0.5 | 84 | 42 | 11.5 | 8.52 | 28.2428 | Yes | 36
3 | 0.5 | 84 | 42 | 11 | 8.51 | 29.1088 | Yes | 36
4 | 0.5 | 84 | 42 | 10.4 | 8.49 | 30.0987 | Yes | 36
5 | 0.5 | 84 | 42 | 9.9 | 8.53 | 31.5939 | Yes | 36
6 | 0.5 | 84 | 42 | 9.2 | 8.51 | 32.8988 | Yes | 36
7 | 0.5 | 84 | 42 | 8.5 | 8.5 | 34.3867 | Yes | 36
8 | 0.5 | 84 | 42 | 7.4 | 8.54 | 37.633 | Yes | 36
9 | 0.5 | 84 | 42 | 6.1 | 8.51 | 40.7153 | Yes | 36
10 | 0.6 | 84 | 50.4 | 5.7 | 8.5 | 42.2026 | Yes | 36
11 | 0.6 | 84 | 50.4 | 5.3 | 8.53 | 43.8747 | Yes | 36
12 | 0.6 | 84 | 50.4 | 5 | 8.55 | 45.1326 | Yes | 36
13 | 0.6 | 84 | 50.4 | 4.7 | 8.51 | 45.4062 | Yes | 36
14 | 0.6 | 84 | 50.4 | 4.6 | 8.53 | 46.0639 | Yes | 36
15 | 0.6 | 84 | 50.4 | 4.2 | 8.54 | 47.5424 | Yes | 36
16 | 0.6 | 84 | 50.4 | 4.1 | 8.51 | 47.3443 | Yes | 36
17 | 0.6 | 84 | 50.4 | 4 | 8.49 | 47.3226 | Yes | 36
18 | 0.6 | 84 | 50.4 | 4 | 8.48 | 47.1471 | Yes | 36
19 | 0.6 | 84 | 50.4 | 4 | 8.5 | 47.4988 | Yes | 36
20 | 0.6 | 84 | 50.4 | 4 | 8.53 | 48.0315 | Yes | 36
21 | 0.6 | 84 | 50.4 | 3.8 | 8.52 | 48.5258 | Yes | 36
22 | 0.6 | 84 | 50.4 | 3.8 | 8.54 | 48.8883 | Yes | 36
23 | 0.7 | 84 | 58.8 | 3.5 | 8.52 | 50.15 | Yes | 36
24 | 0.7 | 84 | 58.8 | 3.2 | 8.5 | 50.833 | Yes | 36
25 | 0.7 | 84 | 58.8 | 3 | 8.51 | 51.7421 | Yes | 36
26 | 0.7 | 84 | 58.8 | 3 | 8.54 | 52.3246 | Yes | 36
27 | 0.7 | 84 | 58.8 | 3 | 8.52 | 51.9355 | Yes | 36
28 | 0.7 | 84 | 58.8 | 3 | 8.51 | 51.7421 | Yes | 36
29 | 0.7 | 84 | 58.8 | 3 | 8.54 | 52.3246 | Yes | 36
30 | 0.7 | 84 | 58.8 | 3 | 8.55 | 52.5203 | Yes | 36
31 |  | 84 | [5 empty] | 36
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised October 2013
PAGE 2 of 2