## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Linn
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2022-12-01
System Name: | Big Lake Youth Camp |  |  | ID#: 41 | 90958 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 15 | 12 | 3 | 30 | 0.15 | 0.15
2 | 15 | 12 | 3 | 30 | 0.13 | 0.13
3 | 15 | 12 | 3 | 30 | 0.14 | 0.14
4 | 15 | 12 | 3 | 30 | 0.15 | 0.15
5 | 17 | 12 | 5 | 30 | 0.17 | 0.17
6 | 17 | 12 | 5 | 30 | 0.16 | 0.16
7 | 17 | 12 | 5 | 30 | 0.14 | 0.14
8 | 18 | 12 | 6 | 30 | 0.15 | 0.15
9 | 18 | 12 | 6 | 30 | 0.13 | 0.13
10 | 19 | 12 | 7 | 30 | 0.12 | 0.12
11 | 20 | 12 | 8 | 30 | 0.14 | 0.14
12 | 20 | 12 | 8 | 30 | 0.13 | 0.13
13 | 22 | 12 | 10 | 30 | 0.15 | 0.15
14 | 22 | 12 | 10 | 30 | 0.17 | 0.17
15 | 22 | 12 | 10 | 30 | 0.16 | 0.16
16 | 22 | 12 | 10 | 30 | 0.14 | 0.14
17 | 22 | 12 | 10 | 30 | 0.13 | 0.13
18 | 22 | 12 | 10 | 30 | 0.15 | 0.15
19 | 22 | 12 | 10 | 30 | 0.14 | 0.14
20 | 22 | 12 | 10 | 30 | 0.16 | 0.16
21 | 22 | 12 | 10 | 30 | 0.17 | 0.17
22 | 22 | 12 | 10 | 30 | 0.14 | 0.14
23 | 25 | 12 | 13 | 30 | 0.15 | 0.15
24 | 25 | 12 | 13 | 30 | 0.14 | 0.14
25 | 25 | 12 | 13 | 30 | 0.15 | 0.15
26 | 28 | 12 | 16 | 30 | 0.16 | 0.16
27 | 28 | 12 | 16 | 30 | 0.17 | 0.17
28 | 28 | 12 | 16 | 30 | 0.15 | 0.15
29 | 28 | 12 | 16 | 30 | 0.16 | 0.16
30 | 28 | 12 | 16 | 30 | 0.14 | 0.14
31 | 28 | 12 | 16 | 30 | 0.13 | 0.13
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME:Ross von Pohle
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE:Ross von Pohle |  | DATE:1-10-2023
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: (503)850-3576 |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Big Lake Youth Camp |  | ID#: 41 | 90958 | Month/Year: | 2022-12-01 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.7 | 84 | 58.8 | 3 | 8.55 | 52.5203 | Yes | 36
2 | 0.7 | 84 | 58.8 | 3 | 8.54 | 52.3246 | Yes | 36
3 | 0.7 | 84 | 58.8 | 3 | 8.55 | 52.5203 | Yes | 36
4 | 0.7 | 84 | 58.8 | 3 | 8.53 | 52.1297 | Yes | 36
5 | 0.7 | 84 | 58.8 | 3 | 8.53 | 52.1297 | Yes | 36
6 | 0.7 | 84 | 58.8 | 3 | 8.51 | 51.7421 | Yes | 36
7 | 0.7 | 84 | 58.8 | 3 | 8.53 | 52.1297 | Yes | 36
8 | 0.7 | 84 | 58.8 | 3 | 8.52 | 51.9355 | Yes | 36
9 | 0.7 | 84 | 58.8 | 3 | 8.5 | 51.5495 | Yes | 36
10 | 0.7 | 84 | 58.8 | 3 | 8.51 | 51.7421 | Yes | 36
11 | 0.7 | 84 | 58.8 | 2.9 | 8.52 | 52.3005 | Yes | 36
12 | 0.7 | 84 | 58.8 | 2.9 | 8.5 | 51.9116 | Yes | 36
13 | 0.7 | 84 | 58.8 | 2.9 | 8.49 | 51.7183 | Yes | 36
14 | 0.7 | 84 | 58.8 | 2.9 | 8.47 | 51.3339 | Yes | 36
15 | 0.7 | 84 | 58.8 | 2.9 | 8.46 | 51.1428 | Yes | 36
16 | 0.7 | 84 | 58.8 | 2.9 | 8.48 | 51.5257 | Yes | 36
17 | 0.7 | 84 | 58.8 | 2.9 | 8.45 | 50.9525 | Yes | 36
18 | 0.7 | 84 | 58.8 | 2.9 | 8.46 | 51.1428 | Yes | 36
19 | 0.7 | 84 | 58.8 | 2.8 | 8.47 | 51.6945 | Yes | 36
20 | 0.7 | 84 | 58.8 | 2.8 | 8.44 | 51.1193 | Yes | 36
21 | 0.7 | 84 | 58.8 | 2.8 | 8.42 | 50.7396 | Yes | 36
22 | 0.7 | 84 | 58.8 | 2.8 | 8.43 | 50.9291 | Yes | 36
23 | 0.7 | 84 | 58.8 | 2.8 | 8.44 | 51.1193 | Yes | 36
24 | 0.7 | 84 | 58.8 | 2.7 | 8.454 | 51.7479 | Yes | 36
25 | 0.7 | 84 | 58.8 | 2.7 | 8.43 | 51.2867 | Yes | 36
26 | 0.7 | 84 | 58.8 | 2.7 | 8.42 | 51.0958 | Yes | 36
27 | 0.7 | 84 | 58.8 | 2.7 | 8.43 | 51.2867 | Yes | 36
28 | 0.7 | 84 | 58.8 | 2.7 | 8.45 | 51.6707 | Yes | 36
29 | 0.7 | 84 | 58.8 | 2.7 | 8.42 | 51.0958 | Yes | 36
30 | 0.7 | 84 | 58.8 | 2.7 | 8.43 | 51.2867 | Yes | 36
31 | 0.7 | 84 | 58.8 | 2.6 | 8.42 | 51.4546 | Yes | 36
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised October 2013
PAGE 2 of 2