## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Linn
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2023-01-01
System Name: | Big Lake Youth Camp |  |  | ID#: 41 | 90958 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 28 | 12 | 16 | 30 | 0.13 | 0.13
2 | 28 | 12 | 16 | 30 | 0.11 | 0.11
3 | 28 | 12 | 16 | 30 | 0.14 | 0.14
4 | 28 | 12 | 16 | 30 | 0.12 | 0.12
5 | 28 | 12 | 16 | 30 | 0.13 | 0.13
6 | 28 | 12 | 16 | 30 | 0.15 | 0.15
7 | 28 | 12 | 16 | 30 | 0.13 | 0.13
8 | 28 | 12 | 16 | 30 | 0.12 | 0.12
9 | 28 | 12 | 16 | 30 | 0.14 | 0.14
10 | 28 | 12 | 16 | 30 | 0.15 | 0.15
11 | 28 | 12 | 16 | 30 | 0.16 | 0.16
12 | 28 | 12 | 16 | 30 | 0.13 | 0.13
13 | 28 | 12 | 16 | 30 | 0.14 | 0.14
14 | 28 | 12 | 16 | 30 | 0.12 | 0.12
15 | 28 | 12 | 16 | 30 | 0.12 | 0.12
16 | 28 | 12 | 16 | 30 | 0.13 | 0.13
17 | 28 | 12 | 16 | 30 | 0.1 | 0.1
18 | 30 | 12 | 18 | 30 | 0.11 | 0.11
19 | 30 | 14 | 16 | 30 | 0.1 | 0.1
20 | 30 | 14 | 16 | 30 | 0.12 | 0.12
21 | 30 | 14 | 16 | 30 | 0.13 | 0.13
22 | 30 | 14 | 16 | 30 | 0.12 | 0.12
23 | 30 | 14 | 16 | 30 | 0.14 | 0.14
24 | 30 | 14 | 16 | 30 | 0.13 | 0.13
25 | 30 | 14 | 16 | 30 | 0.15 | 0.15
26 | 30 | 14 | 16 | 30 | 0.13 | 0.13
27 | 30 | 14 | 16 | 30 | 0.12 | 0.12
28 | 30 | 14 | 16 | 30 | 0.13 | 0.13
29 | 30 | 14 | 16 | 30 | 0.14 | 0.14
30 | 30 | 14 | 16 | 30 | 0.12 | 0.12
31 | 30 | 14 | 16 | 30 | 0.14 | 0.14
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME:Ross von Pohle
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | DATE:2/10/2023
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: ( ) |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Big Lake Youth Camp |  | ID#: 41 | 90958 | Month/Year: | 2023-01-01 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.7 | 84 | 58.8 | 2.6 | 8.42 | 51.4546 | Yes | 36
2 | 0.7 | 84 | 58.8 | 2.6 | 8.4 | 51.0723 | Yes | 36
3 | 0.7 | 84 | 58.8 | 2.6 | 8.43 | 51.6469 | Yes | 36
4 | 0.7 | 84 | 58.8 | 2.6 | 8.41 | 51.2631 | Yes | 36
5 | 0.7 | 84 | 58.8 | 2.6 | 8.44 | 51.84 | Yes | 36
6 | 0.7 | 84 | 58.8 | 2.6 | 8.42 | 51.4546 | Yes | 36
7 | 0.7 | 84 | 58.8 | 2.6 | 8.43 | 51.6469 | Yes | 36
8 | 0.7 | 84 | 58.8 | 2.6 | 8.43 | 51.6469 | Yes | 36
9 | 0.7 | 84 | 58.8 | 2.6 | 8.41 | 51.2631 | Yes | 36
10 | 0.7 | 84 | 58.8 | 2.6 | 8.42 | 51.4546 | Yes | 36
11 | 1 | 84 | 84 | 2.6 | 8.43 | 53.5395 | Yes | 36
12 | 1 | 84 | 84 | 2.6 | 8.44 | 53.7399 | Yes | 36
13 | 1 | 84 | 84 | 2.6 | 8.45 | 53.9411 | Yes | 36
14 | 1 | 84 | 84 | 2.6 | 8.43 | 53.5395 | Yes | 36
15 | 1 | 84 | 84 | 2.6 | 8.46 | 54.1431 | Yes | 36
16 | 1 | 84 | 84 | 2.6 | 8.44 | 53.7399 | Yes | 36
17 | 1 | 84 | 84 | 2.6 | 8.45 | 53.9411 | Yes | 36
18 | 1 | 84 | 84 | 2.6 | 8.43 | 53.5395 | Yes | 36
19 | 1 | 84 | 84 | 2.6 | 8.41 | 53.141 | Yes | 36
20 | 1 | 84 | 84 | 2.6 | 8.4 | 52.9429 | Yes | 36
21 | 1 | 84 | 84 | 2.6 | 8.39 | 52.7456 | Yes | 36
22 | 1 | 84 | 84 | 2.6 | 8.42 | 53.3399 | Yes | 36
23 | 1 | 84 | 84 | 2.6 | 8.45 | 53.9411 | Yes | 36
24 | 1 | 84 | 84 | 2.6 | 8.44 | 53.7399 | Yes | 36
25 | 1 | 84 | 84 | 2.6 | 8.41 | 53.141 | Yes | 36
26 | 1 | 84 | 84 | 2.6 | 8.421 | 53.3598 | Yes | 36
27 | 1 | 84 | 84 | 2.6 | 8.43 | 53.5395 | Yes | 36
28 | 1 | 84 | 84 | 2.6 | 8.42 | 53.3399 | Yes | 36
29 | 1 | 84 | 84 | 2.6 | 8.4 | 52.9429 | Yes | 36
30 | 1 | 84 | 84 | 2.6 | 8.42 | 53.3399 | Yes | 36
31 | 1 | 84 | 84 | 2.6 | 8.43 | 53.5395 | Yes | 36
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised October 2013
PAGE 2 of 2