## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Linn
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2023-03-01
System Name: | Big Lake Youth Camp |  |  | ID#: 41 | 90958 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 8 | 4 | 4 | 30 | 0.15 | 0.15
2 | 8 | 4 | 4 | 30 | 0.17 | 0.17
3 | 8 | 4 | 4 | 30 | 0.16 | 0.16
4 | 8 | 4 | 4 | 30 | 0.15 | 0.15
5 | 8 | 4 | 4 | 30 | 0.13 | 0.13
6 | 10 | 5 | 5 | 30 | 0.17 | 0.17
7 | 10 | 5 | 5 | 30 | 0.19 | 0.19
8 | 10 | 5 | 5 | 30 | 0.14 | 0.14
9 | 12 | 6 | 6 | 30 | 0.17 | 0.17
10 | 12 | 6 | 6 | 30 | 0.16 | 0.16
11 | 13 | 6 | 7 | 30 | 0.19 | 0.19
12 | 13 | 6 | 7 | 30 | 0.17 | 0.17
13 | 13 | 6 | 7 | 30 | 0.14 | 0.14
14 | 15 | 6 | 9 | 30 | 0.15 | 0.15
15 | 15 | 6 | 9 | 30 | 0.13 | 0.13
16 | 15 | 6 | 9 | 30 | 0.11 | 0.11
17 | 16 | 6 | 10 | 30 | 0.15 | 0.15
18 | 16 | 6 | 10 | 30 | 0.17 | 0.17
19 | 16 | 6 | 10 | 30 | 0.16 | 0.16
20 | 19 | 7 | 12 | 30 | 0.14 | 0.14
21 | 19 | 7 | 12 | 30 | 0.18 | 0.18
22 | 20 | 8 | 12 | 30 | 0.2 | 0.2
23 | 20 | 8 | 12 | 30 | 0.21 | 0.21
24 | 22 | 10 | 12 | 30 | 0.19 | 0.19
25 | 25 | 10 | 15 | 30 | 0.23 | 0.23
26 | 28 | 10 | 18 | 30 | 0.21 | 0.21
27 | 30 | 10 | 20 | 30 | 0.24 | 0.24
28 | 33 | 10 | 23 | 30 | 0.26 | 0.26
29 | 36 | 10 | 26 | 30 | 0.24 | 0.24
30 | 38 | 10 | 28 | 30 | 0.23 | 0.23
31 | 40 | 10 | 30 | 30 | 0.26 | 0.26
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME:Ross von Pohle
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | DATE:4/10/2023
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: (503)850-3576 |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Big Lake Youth Camp |  | ID#: 41 | 90958 | Month/Year: | 2023-03-01 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.7 | 80 | 56 | 5.7 | 7.54 | 30.0581 | Yes | 36
2 | 0.7 | 80 | 56 | 5.7 | 7.57 | 30.3861 | Yes | 36
3 | 0.7 | 80 | 56 | 5.7 | 7.61 | 30.8293 | Yes | 36
4 | 0.7 | 80 | 56 | 5.7 | 7.58 | 30.4962 | Yes | 36
5 | 0.7 | 80 | 56 | 5.8 | 7.69 | 31.5214 | Yes | 36
6 | 0.7 | 80 | 56 | 5.8 | 7.64 | 30.9551 | Yes | 36
7 | 0.7 | 80 | 56 | 5.8 | 7.66 | 31.1803 | Yes | 36
8 | 0.8 | 80 | 64 | 5.8 | 7.69 | 31.8913 | Yes | 36
9 | 0.8 | 80 | 64 | 5.8 | 7.74 | 32.476 | Yes | 36
10 | 0.8 | 80 | 64 | 5.8 | 7.76 | 32.7131 | Yes | 36
11 | 0.8 | 80 | 64 | 5.8 | 7.72 | 32.2408 | Yes | 36
12 | 0.8 | 80 | 64 | 5.8 | 7.67 | 31.6605 | Yes | 36
13 | 0.8 | 80 | 64 | 5.8 | 7.64 | 31.3178 | Yes | 36
14 | 0.8 | 80 | 64 | 5.8 | 7.68 | 31.7757 | Yes | 36
15 | 0.8 | 80 | 64 | 5.8 | 7.65 | 31.4316 | Yes | 36
16 | 0.8 | 80 | 64 | 5.8 | 7.67 | 31.6605 | Yes | 36
17 | 0.8 | 80 | 64 | 5.8 | 7.69 | 31.8913 | Yes | 36
18 | 0.8 | 80 | 64 | 5.8 | 7.66 | 31.5459 | Yes | 36
19 | 0.8 | 80 | 64 | 5.9 | 7.61 | 30.7691 | Yes | 36
20 | 0.8 | 80 | 64 | 5.9 | 7.64 | 31.1054 | Yes | 36
21 | 0.8 | 80 | 64 | 5.9 | 7.6 | 30.6579 | Yes | 36
22 | 0.8 | 80 | 64 | 5.9 | 7.57 | 30.3268 | Yes | 36
23 | 0.8 | 80 | 64 | 6 | 7.54 | 29.7967 | Yes | 36
24 | 0.9 | 80 | 72 | 6 | 7.52 | 29.9277 | Yes | 36
25 | 0.9 | 80 | 72 | 6 | 7.55 | 30.2541 | Yes | 36
26 | 0.9 | 80 | 72 | 6 | 7.59 | 30.6953 | Yes | 36
27 | 0.9 | 80 | 72 | 6 | 7.54 | 30.1449 | Yes | 36
28 | 0.9 | 80 | 72 | 6 | 7.57 | 30.4738 | Yes | 36
29 | 0.9 | 80 | 72 | 6.1 | 7.61 | 30.709 | Yes | 36
30 | 0.9 | 80 | 72 | 6.1 | 7.55 | 30.0495 | Yes | 36
31 | 0.9 | 80 | 72 | 6.1 | 7.59 | 30.4875 | Yes | 36
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised October 2013
PAGE 2 of 2