## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Linn
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2023-05-01
System Name: | Big Lake Youth Camp |  |  | ID#: 41 | 90958 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 10 | 10 | 0 | 30 | 0.25 | 0.25
2 | 10 | 10 | 0 | 30 | 0.28 | 0.28
3 | 10 | 10 | 0 | 30 | 0.26 | 0.26
4 | 10 | 10 | 0 | 30 | 0.25 | 0.25
5 | 10 | 10 | 0 | 30 | 0.24 | 0.24
6 | 10 | 10 | 0 | 30 | 0.25 | 0.25
7 | 10 | 10 | 0 | 30 | 0.23 | 0.23
8 | 10 | 10 | 0 | 30 | 0.24 | 0.24
9 | 10 | 10 | 0 | 30 | 0.26 | 0.26
10 | 10 | 10 | 0 | 30 | 0.27 | 0.27
11 | 10 | 10 | 0 | 30 | 0.25 | 0.25
12 | 12 | 10 | 2 | 30 | 0.24 | 0.24
13 | 12 | 10 | 2 | 30 | 0.26 | 0.26
14 | 12 | 10 | 2 | 30 | 0.27 | 0.27
15 | 12 | 10 | 2 | 30 | 0.25 | 0.25
16 | 12 | 10 | 2 | 30 | 0.26 | 0.26
17 | 12 | 10 | 2 | 30 | 0.24 | 0.24
18 | 12 | 10 | 2 | 30 | 0.25 | 0.25
19 | 15 | 10 | 5 | 30 | 0.27 | 0.27
20 | 15 | 10 | 5 | 30 | 0.26 | 0.26
21 | 15 | 10 | 5 | 30 | 0.23 | 0.23
22 | 15 | 10 | 5 | 30 | 0.25 | 0.25
23 | 15 | 10 | 5 | 30 | 0.24 | 0.24
24 | 15 | 10 | 5 | 30 | 0.26 | 0.26
25 | 15 | 10 | 5 | 30 | 0.27 | 0.27
26 | 18 | 10 | 8 | 30 | 0.28 | 0.28
27 | 18 | 10 | 8 | 30 | 0.26 | 0.26
28 | 18 | 10 | 8 | 30 | 0.25 | 0.25
29 | 18 | 10 | 8 | 30 | 0.27 | 0.27
30 | 18 | 10 | 8 | 30 | 0.28 | 0.28
31 | 20 | 10 | 10 | 30 | 0.26 | 0.26
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME:Ross von Pohle
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE:Ross von Pohle |  | DATE:06/10/2023
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: (503)850-3576 |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Big Lake Youth Camp |  | ID#: 41 | 90958 | Month/Year: | 2023-05-01 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.7 | 84 | 58.8 | 6.2 | 7.6 | 29.6928 | Yes | 36
2 | 0.7 | 84 | 58.8 | 6.2 | 7.63 | 30.0165 | Yes | 36
3 | 0.7 | 84 | 58.8 | 6.2 | 7.65 | 30.2344 | Yes | 36
4 | 0.7 | 84 | 58.8 | 6.2 | 7.64 | 30.1253 | Yes | 36
5 | 0.7 | 84 | 58.8 | 6.2 | 7.66 | 30.344 | Yes | 36
6 | 0.7 | 84 | 58.8 | 6.2 | 7.68 | 30.5644 | Yes | 36
7 | 0.7 | 84 | 58.8 | 6.5 | 7.65 | 29.6254 | Yes | 36
8 | 0.7 | 84 | 58.8 | 6.5 | 7.68 | 29.9483 | Yes | 36
9 | 0.7 | 84 | 58.8 | 6.5 | 7.64 | 29.5186 | Yes | 36
10 | 0.7 | 84 | 58.8 | 6.5 | 7.67 | 29.8402 | Yes | 36
11 | 0.7 | 84 | 58.8 | 6.5 | 7.65 | 29.6254 | Yes | 36
12 | 0.7 | 84 | 58.8 | 6.5 | 7.64 | 29.5186 | Yes | 36
13 | 0.7 | 84 | 58.8 | 6.8 | 7.66 | 29.1344 | Yes | 36
14 | 0.7 | 84 | 58.8 | 6.8 | 7.64 | 28.9251 | Yes | 36
15 | 0.7 | 84 | 58.8 | 6.8 | 7.63 | 28.821 | Yes | 36
16 | 0.6 | 84 | 50.4 | 6.8 | 7.66 | 28.7988 | Yes | 36
17 | 0.6 | 84 | 50.4 | 6.8 | 7.69 | 29.112 | Yes | 36
18 | 0.6 | 84 | 50.4 | 6.8 | 7.67 | 28.9028 | Yes | 36
19 | 0.6 | 84 | 50.4 | 6.8 | 7.68 | 29.0072 | Yes | 36
20 | 0.6 | 84 | 50.4 | 6.8 | 7.65 | 28.6952 | Yes | 36
21 | 0.6 | 84 | 50.4 | 6.8 | 7.68 | 29.0072 | Yes | 36
22 | 0.6 | 84 | 50.4 | 7 | 7.66 | 28.4121 | Yes | 36
23 | 0.6 | 84 | 50.4 | 7 | 7.69 | 28.7208 | Yes | 36
24 | 0.6 | 84 | 50.4 | 7 | 7.68 | 28.6175 | Yes | 36
25 | 0.6 | 84 | 50.4 | 7 | 7.67 | 28.5146 | Yes | 36
26 | 0.6 | 84 | 50.4 | 7 | 7.69 | 28.7208 | Yes | 36
27 | 0.6 | 84 | 50.4 | 7 | 7.66 | 28.4121 | Yes | 36
28 | 0.6 | 84 | 50.4 | 7 | 7.65 | 28.3101 | Yes | 36
29 | 0.6 | 84 | 50.4 | 7 | 7.67 | 28.5146 | Yes | 36
30 | 0.6 | 84 | 50.4 | 7 | 7.66 | 28.4121 | Yes | 36
31 | 0.6 | 84 | 50.4 | 7.1 | 7.64 | 28.0186 | Yes | 36
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised October 2013
PAGE 2 of 2