## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Linn
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2023-08-01
System Name: | Big Lake Youth Camp |  |  | ID#: 41 | 90958 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 4 | 8 | -4 | 30 | 0.12 | 0.12
2 | 4 | 8 | -4 | 30 | 0.14 | 0.14
3 | 4 | 8 | -4 | 30 | 0.12 | 0.12
4 | 10 | 8 | 2 | 30 | 0.13 | 0.13
5 | 15 | 8 | 7 | 30 | 0.15 | 0.15
6 | 19 | 10 | 9 | 30 | 0.17 | 0.17
7 | 23 | 10 | 13 | 30 | 0.19 | 0.19
8 | 35 | 10 | 25 | 30 | 0.18 | 0.18
9 | 38 | 10 | 28 | 30 | 0.25 | 0.25
10 | 40 | 10 | 30 | 30 | 0.29 | 0.29
11 | 10 | 6 | 4 | 30 | 0.27 | 0.27
12 | 10 | 6 | 4 | 30 | 0.28 | 0.28
13 | 18 | 6 | 12 | 30 | 0.26 | 0.26
14 | 22 | 6 | 16 | 30 | 0.24 | 0.24
15 | 25 | 6 | 19 | 30 | 0.25 | 0.25
16 | 28 | 6 | 22 | 30 | 0.22 | 0.22
17 | 34 | 6 | 28 | 30 | 0.21 | 0.21
18 | 36 | 6 | 30 | 30 | 0.23 | 0.23
19 | 6 | 4 | 2 | 30 | 0.25 | 0.25
20 | 6 | 4 | 2 | 30 | 0.24 | 0.24
21 | 6 | 4 | 2 | 30 | 0.27 | 0.27
22 | 6 | 4 | 2 | 30 | 0.24 | 0.24
23 | 6 | 4 | 2 | 30 | 0.26 | 0.26
24 | 8 | 6 | 2 | 30 | 0.27 | 0.27
25 | 8 | 6 | 2 | 30 | 0.25 | 0.25
26 | 8 | 6 | 2 | 30 | 0.23 | 0.23
27 | 8 | 6 | 2 | 30 | 0.28 | 0.28
28 | 8 | 6 | 2 | 30 | 0.31 | 0.31
29 | 8 | 6 | 2 | 30 | 0.29 | 0.29
30 | 8 | 6 | 2 | 30 | 0.32 | 0.32
31 | 8 | 6 | 2 | 30 | 0.3 | 0.3
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME:Ross von Pohle
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | DATE:09/10/2023
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: (503)850-3576 |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Big Lake Youth Camp |  | ID#: 41 | 90958 | Month/Year: | 2023-08-01 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.5 | 84 | 42 | 20.2 | 9.23 | 20.7602 | Yes | 36
2 | 0.6 | 84 | 50.4 | 20 | 9.21 | 21.1206 | Yes | 36
3 | 0.6 | 84 | 50.4 | 20 | 9.24 | 21.355 | Yes | 36
4 | 0.6 | 84 | 50.4 | 20.1 | 9.2 | 20.904 | Yes | 36
5 | 0.6 | 84 | 50.4 | 20.1 | 9.16 | 20.5985 | Yes | 36
6 | 0.6 | 84 | 50.4 | 19.9 | 9.14 | 20.7202 | Yes | 36
7 | 0.7 | 84 | 58.8 | 19.7 | 9.17 | 21.4713 | Yes | 36
8 | 0.7 | 84 | 58.8 | 19.5 | 9.13 | 21.4398 | Yes | 36
9 | 0.7 | 84 | 58.8 | 19.4 | 9.09 | 21.267 | Yes | 36
10 | 0.9 | 84 | 75.6 | 19.4 | 9.02 | 21.2006 | Yes | 36
11 | 0.9 | 84 | 75.6 | 19.5 | 9.04 | 21.2161 | Yes | 36
12 | 0.9 | 84 | 75.6 | 19.7 | 9.02 | 20.7833 | Yes | 36
13 | 0.9 | 84 | 75.6 | 19.9 | 9.06 | 20.8138 | Yes | 36
14 | 0.9 | 84 | 75.6 | 19.8 | 9.01 | 20.5701 | Yes | 36
15 | 0.9 | 84 | 75.6 | 20 | 9.02 | 20.3741 | Yes | 36
16 | 0.9 | 84 | 75.6 | 20.2 | 9.01 | 20.0317 | Yes | 36
17 | 0.9 | 84 | 75.6 | 20.4 | 9.03 | 19.9139 | Yes | 36
18 | 0.9 | 84 | 75.6 | 20 | 9 | 20.2246 | Yes | 36
19 | 0.9 | 84 | 75.6 | 19.6 | 9.01 | 20.8446 | Yes | 36
20 | 0.9 | 84 | 75.6 | 19.3 | 9.04 | 21.4991 | Yes | 36
21 | 0.7 | 84 | 58.8 | 19 | 9.02 | 21.2828 | Yes | 36
22 | 0.7 | 84 | 58.8 | 18.6 | 9.01 | 21.774 | Yes | 36
23 | 0.6 | 84 | 50.4 | 18.1 | 9 | 22.1721 | Yes | 36
24 | 0.8 | 84 | 67.2 | 18.1 | 9.05 | 23.0995 | Yes | 36
25 | 0.8 | 84 | 67.2 | 18.1 | 9.09 | 23.4414 | Yes | 36
26 | 0.9 | 84 | 75.6 | 18.3 | 9.12 | 23.6554 | Yes | 36
27 | 0.9 | 84 | 75.6 | 18.2 | 9.14 | 23.9878 | Yes | 36
28 | 0.9 | 84 | 75.6 | 18.1 | 9.17 | 24.4143 | Yes | 36
29 | 0.9 | 84 | 75.6 | 18 | 9.15 | 24.3964 | Yes | 36
30 | 0.9 | 84 | 75.6 | 18.1 | 9.12 | 23.9702 | Yes | 36
31 | 0.9 | 84 | 75.6 | 18.2 | 9.16 | 24.1646 | Yes | 36
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised October 2013
PAGE 2 of 2