## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Linn
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2023-09-01
System Name: | Big Lake Youth Camp |  |  | ID#: 41 | 90958 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 8 | 6 | 2 | 30 | 0.3 | 0.3
2 | 10 | 6 | 4 | 30 | 0.29 | 0.29
3 | 12 | 6 | 6 | 30 | 0.27 | 0.27
4 | 12 | 6 | 6 | 30 | 0.28 | 0.28
5 | 12 | 6 | 6 | 30 | 0.26 | 0.26
6 | 15 | 6 | 9 | 30 | 0.24 | 0.24
7 | 12 | 6 | 6 | 30 | 0.27 | 0.27
8 | 17 | 6 | 11 | 30 | 0.28 | 0.28
9 | 20 | 6 | 14 | 30 | 0.24 | 0.24
10 | 22 | 6 | 16 | 30 | 0.23 | 0.23
11 | 28 | 6 | 22 | 30 | 0.25 | 0.25
12 | 30 | 6 | 24 | 30 | 0.27 | 0.27
13 | 40 | 10 | 30 | 30 | 0.26 | 0.26
14 | 4 | 8 | -4 | 30 | 0.23 | 0.23
15 | 4 | 8 | -4 | 30 | 0.2 | 0.2
16 | 4 | 8 | -4 | 30 | 0.21 | 0.21
17 | 4 | 8 | -4 | 30 | 0.19 | 0.19
18 | 4 | 8 | -4 | 30 | 0.17 | 0.17
19 | 4 | 8 | -4 | 30 | 0.14 | 0.14
20 | 6 | 8 | -2 | 30 | 0.15 | 0.15
21 | 6 | 8 | -2 | 30 | 0.18 | 0.18
22 | 6 | 8 | -2 | 30 | 0.16 | 0.16
23 | 8 | 8 | 0 | 30 | 0.14 | 0.14
24 | 8 | 8 | 0 | 30 | 0.13 | 0.13
25 | 8 | 8 | 0 | 30 | 0.15 | 0.15
26 | 12 | 8 | 4 | 30 | 0.14 | 0.14
27 | 12 | 8 | 4 | 30 | 0.16 | 0.16
28 | 16 | 8 | 8 | 30 | 0.17 | 0.17
29 | 16 | 8 | 8 | 30 | 0.15 | 0.15
30 | 18 | 8 | 10 | 30 | 0.14 | 0.14
31 |  |  |  | 30
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes / No | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes / No | Yes / No | Yes / No
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME:
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | DATE:
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: ( ) |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Big Lake Youth Camp |  | ID#: 41 | 90958 | Month/Year: | 2023-09-01 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.9 | 84 | 75.6 | 18.2 | 9.16 | 24.1646 | Yes | 36
2 | 1 | 84 | 84 | 18 | 9.15 | 24.6733 | Yes | 36
3 | 1 | 84 | 84 | 18.1 | 9.13 | 24.3315 | Yes | 36
4 | 1 | 84 | 84 | 17.9 | 9.14 | 24.7459 | Yes | 36
5 | 1 | 84 | 84 | 17.7 | 9.16 | 25.2596 | Yes | 36
6 | 1 | 84 | 84 | 17.6 | 9.17 | 25.5205 | Yes | 36
7 | 1 | 84 | 84 | 17.4 | 9.15 | 25.6708 | Yes | 36
8 | 1 | 84 | 84 | 17 | 9.12 | 26.0694 | Yes | 36
9 | 1 | 84 | 84 | 16.7 | 9.15 | 26.8848 | Yes | 36
10 | 1 | 84 | 84 | 16.2 | 9.13 | 27.5835 | Yes | 36
11 | 1 | 84 | 84 | 15.9 | 9.16 | 28.4455 | Yes | 36
12 | 1 | 84 | 84 | 15.6 | 9.14 | 28.802 | Yes | 36
13 | 1 | 84 | 84 | 15.3 | 9.17 | 29.7015 | Yes | 36
14 | 1.2 | 84 | 100.8 | 15.4 | 9.2 | 30.511 | Yes | 36
15 | 1.4 | 84 | 117.6 | 15.5 | 9.21 | 31.1139 | Yes | 36
16 | 1.8 | 84 | 151.2 | 15.2 | 9.26 | 33.8059 | Yes | 36
17 | 2 | 84 | 168 | 15.4 | 9.29 | 34.4981 | Yes | 36
18 | 2 | 84 | 168 | 15.5 | 9.32 | 34.6496 | Yes | 36
19 | 2.2 | 84 | 184.8 | 15.6 | 9.44 | 36.781 | Yes | 36
20 | 2 | 84 | 168 | 15.5 | 9.4 | 35.6768 | Yes | 36
21 | 2 | 84 | 168 | 15.5 | 9.41 | 35.8073 | Yes | 36
22 | 1.8 | 84 | 151.2 | 15.4 | 9.39 | 34.9867 | Yes | 36
23 | 1.8 | 84 | 151.2 | 15.2 | 9.37 | 35.1919 | Yes | 36
24 | 1.8 | 84 | 151.2 | 15.2 | 9.33 | 34.6815 | Yes | 36
25 | 1.5 | 84 | 126 | 15 | 9.31 | 33.729 | Yes | 36
26 | 1.5 | 84 | 126 | 15 | 9.34 | 34.1007 | Yes | 36
27 | 1.1 | 84 | 92.4 | 14.8 | 9.29 | 32.4358 | Yes | 36
28 | 1.1 | 84 | 92.4 | 14.7 | 9.25 | 32.176 | Yes | 36
29 | 1.1 | 84 | 92.4 | 14.5 | 9.21 | 32.1291 | Yes | 36
30 | 1.1 | 84 | 92.4 | 14.2 | 9.19 | 32.5312 | Yes | 36
31 |  | 84 | [5 empty] | 36
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised October 2013
PAGE 2 of 2