## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Linn
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2023-10-01
System Name: | Big Lake Youth Camp |  |  | ID#: 41 | 90958 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 18 | 8 | 10 | 30 | 0.15 | 0.15
2 | 20 | 8 | 12 | 30 | 0.12 | 0.121
3 | 20 | 8 | 12 | 30 | 0.14 | 0.14
4 | 22 | 8 | 14 | 30 | 0.11 | 0.11
5 | 25 | 10 | 15 | 30 | 0.13 | 0.13
6 | 28 | 10 | 18 | 30 | 0.15 | 0.15
7 | 30 | 10 | 20 | 30 | 0.16 | 0.16
8 | 35 | 10 | 25 | 30 | 0.14 | 0.14
9 | 38 | 10 | 28 | 30 | 0.13 | 0.13
10 | 40 | 10 | 30 | 30 | 0.17 | 0.17
11 | 7 | 7 | 0 | 30 | 0.15 | 0.15
12 | 7 | 7 | 0 | 30 | 0.13 | 0.13
13 | 7 | 7 | 0 | 30 | 0.14 | 0.14
14 | 7 | 7 | 0 | 30 | 0.12 | 0.12
15 | 10 | 8 | 2 | 30 | 0.16 | 0.16
16 | 10 | 8 | 2 | 30 | 0.15 | 0.15
17 | 10 | 8 | 2 | 30 | 0.18 | 0.18
18 | 12 | 8 | 4 | 30 | 0.14 | 0.14
19 | 12 | 9 | 3 | 30 | 0.16 | 0.16
20 | 15 | 9 | 6 | 30 | 0.17 | 0.17
21 | 15 | 9 | 6 | 30 | 0.19 | 0.19
22 | 17 | 10 | 7 | 30 | 0.16 | 0.16
23 | 17 | 10 | 7 | 30 | 0.15 | 0.15
24 | 20 | 12 | 8 | 30 | 0.17 | 0.17
25 | 23 | 12 | 11 | 30 | 0.18 | 0.18
26 | 25 | 17 | 8 | 30 | 0.15 | 0.15
27 | 29 | 17 | 12 | 30 | 0.17 | 0.17
28 | 30 | 20 | 10 | 30 | 0.2 | 0.2
29 | 40 | 20 | 20 | 30 | 0.18 | 0.18
30 | 50 | 20 | 30 | 30 | 0.13 | 0.13
31 | 7 | 10 | -3 | 30 | 0.15 | 0.15
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME:Ross von Pohle
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE:Ross von Pohle |  | DATE:11/10/2023
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: (503)850-3576 |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Big Lake Youth Camp |  | ID#: 41 | 90958 | Month/Year: | 2023-10-01 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1 | 84 | 84 | 14 | 9.19 | 32.5938 | Yes | 36
2 | 1 | 84 | 84 | 13.7 | 9.15 | 32.7612 | Yes | 36
3 | 0.8 | 84 | 67.2 | 13.5 | 9.16 | 32.5763 | Yes | 36
4 | 0.8 | 84 | 67.2 | 13.2 | 9.09 | 32.3865 | Yes | 36
5 | 0.6 | 84 | 50.4 | 13.1 | 9.02 | 31.0701 | Yes | 36
6 | 0.6 | 84 | 50.4 | 13.1 | 9 | 30.8436 | Yes | 36
7 | 0.6 | 84 | 50.4 | 13 | 8.95 | 30.4848 | Yes | 36
8 | 0.6 | 84 | 50.4 | 13 | 8.97 | 30.7086 | Yes | 36
9 | 0.6 | 84 | 50.4 | 12.8 | 8.92 | 30.5519 | Yes | 36
10 | 0.4 | 84 | 33.6 | 12.6 | 8.86 | 29.611 | Yes | 36
11 | 0.7 | 84 | 58.8 | 12.4 | 8.84 | 30.5258 | Yes | 36
12 | 0.7 | 84 | 58.8 | 12.2 | 8.89 | 31.5097 | Yes | 36
13 | 0.7 | 84 | 58.8 | 12 | 8.85 | 31.4815 | Yes | 36
14 | 0.7 | 84 | 58.8 | 11.8 | 8.86 | 32.0294 | Yes | 36
15 | 0.7 | 84 | 58.8 | 11.5 | 8.83 | 32.337 | Yes | 36
16 | 0.7 | 84 | 58.8 | 11.2 | 8.81 | 32.7667 | Yes | 36
17 | 0.9 | 84 | 75.6 | 11 | 8.84 | 34.379 | Yes | 36
18 | 0.9 | 84 | 75.6 | 10.7 | 8.82 | 34.8377 | Yes | 36
19 | 0.9 | 84 | 75.6 | 10.5 | 8.85 | 35.7086 | Yes | 36
20 | 0.9 | 84 | 75.6 | 10.2 | 8.83 | 36.1863 | Yes | 36
21 | 0.9 | 84 | 75.6 | 9.9 | 8.86 | 37.3493 | Yes | 36
22 | 0.9 | 84 | 75.6 | 9.6 | 8.85 | 37.9896 | Yes | 36
23 | 0.9 | 84 | 75.6 | 9.1 | 8.89 | 39.9065 | Yes | 36
24 | 0.9 | 84 | 75.6 | 9 | 8.87 | 39.8883 | Yes | 36
25 | 0.9 | 84 | 75.6 | 8.6 | 8.88 | 41.159 | Yes | 36
26 | 1 | 84 | 84 | 8.2 | 8.85 | 42.3492 | Yes | 36
27 | 1 | 84 | 84 | 7.8 | 8.86 | 43.7026 | Yes | 36
28 | 1 | 84 | 84 | 7.1 | 8.84 | 45.5436 | Yes | 36
29 | 1 | 84 | 84 | 7 | 8.87 | 46.3753 | Yes | 36
30 | 1.2 | 84 | 100.8 | 6.8 | 8.88 | 48.3424 | Yes | 36
31 | 1.2 | 84 | 100.8 | 6.8 | 8.86 | 47.9842 | Yes | 36
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised October 2013
PAGE 2 of 2