## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Linn
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2023-11-01
System Name: | Big Lake Youth Camp |  |  | ID#: 41 | 90958 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 7 | 10 | -3 | 30 | 0.15 | 0.15
2 | 7 | 10 | -3 | 30 | 0.19 | 0.19
3 | 7 | 10 | -3 | 30 | 0.21 | 0.21
4 | 7 | 10 | -3 | 30 | 0.23 | 0.23
5 | 7 | 11 | -4 | 30 | 0.25 | 0.25
6 | 7 | 11 | -4 | 30 | 0.27 | 0.27
7 | 7 | 12 | -5 | 30 | 0.26 | 0.26
8 | 8 | 13 | -5 | 30 | 0.25 | 0.25
9 | 8 | 13 | -5 | 30 | 0.23 | 0.23
10 | 8 | 13 | -5 | 30 | 0.24 | 0.24
11 | 8 | 13 | -5 | 30 | 0.21 | 0.21
12 | 9 | 14 | -5 | 30 | 0.23 | 0.23
13 | 9 | 14 | -5 | 30 | 0.22 | 0.22
14 | 9 | 14 | -5 | 30 | 0.24 | 0.24
15 | 10 | 14 | -4 | 30 | 0.21 | 0.21
16 | 10 | 14 | -4 | 30 | 0.19 | 0.19
17 | 10 | 14 | -4 | 30 | 0.21 | 0.21
18 | 10 | 14 | -4 | 30 | 0.2 | 0.2
19 | 10 | 14 | -4 | 30 | 0.19 | 0.19
20 | 10 | 14 | -4 | 30 | 0.13 | 0.13
21 | 12 | 14 | -2 | 30 | 0.12 | 0.12
22 | 12 | 14 | -2 | 30 | 0.13 | 0.13
23 | 13 | 16 | -3 | 30 | 0.15 | 0.15
24 | 13 | 16 | -3 | 30 | 0.12 | 0.12
25 | 14 | 16 | -2 | 30 | 0.12 | 0.12
26 | 14 | 16 | -2 | 30 | 0.11 | 0.11
27 | 16 | 18 | -2 | 30 | 0.1 | 0.1
28 | 16 | 20 | -4 | 30 | 0.1 | 0.1
29 | 16 | 20 | -4 | 30 | 0.1 | 0.1
30 | 17 | 21 | -4 | 30 | 0.1 | 0.1
31 |  |  |  | 30
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME:Randy Stroud
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE:Randy Stroud |  | DATE:12/1/2023
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: (503)850-3576 |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Big Lake Youth Camp |  | ID#: 41 | 90958 | Month/Year: | 2023-11-01 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.2 | 84 | 100.8 | 6.8 | 8.88 | 48.3424 | Yes | 36
2 | 1.2 | 84 | 100.8 | 7.2 | 8.9 | 47.3629 | Yes | 36
3 | 1.3 | 84 | 109.2 | 7.5 | 9.09 | 50.3777 | Yes | 36
4 | 1.3 | 84 | 109.2 | 7.8 | 9 | 47.708 | Yes | 36
5 | 1.4 | 84 | 117.6 | 8 | 8.9 | 45.8767 | Yes | 36
6 | 1.4 | 84 | 117.6 | 8.2 | 9.1 | 48.7314 | Yes | 36
7 | 1.5 | 84 | 126 | 8.4 | 9.2 | 50.4787 | Yes | 36
8 | 1.5 | 84 | 126 | 8.3 | 9.18 | 50.4555 | Yes | 36
9 | 1.5 | 84 | 126 | 8.1 | 9.16 | 50.7863 | Yes | 36
10 | 1.5 | 84 | 126 | 8 | 9.12 | 50.3859 | Yes | 36
11 | 1.5 | 84 | 126 | 8 | 9.13 | 50.5741 | Yes | 36
12 | 1.5 | 84 | 126 | 8 | 9.1 | 50.0119 | Yes | 36
13 | 1.6 | 84 | 134.4 | 8 | 9.11 | 50.8033 | Yes | 36
14 | 1.6 | 84 | 134.4 | 8 | 9.09 | 50.426 | Yes | 36
15 | 1.6 | 84 | 134.4 | 7.9 | 9.12 | 51.3511 | Yes | 36
16 | 1.6 | 84 | 134.4 | 7.9 | 9.1 | 50.9696 | Yes | 36
17 | 1.6 | 84 | 134.4 | 7.8 | 9.08 | 50.9462 | Yes | 36
18 | 1.6 | 84 | 134.4 | 7.9 | 9.1 | 50.9696 | Yes | 36
19 | 1.3 | 84 | 109.2 | 8.1 | 9.09 | 48.3096 | Yes | 36
20 | 1.5 | 84 | 126 | 8.1 | 9.08 | 49.2951 | Yes | 36
21 | 1.5 | 84 | 126 | 7.9 | 9.06 | 49.6179 | Yes | 36
22 | 1.4 | 84 | 117.6 | 7.5 | 9.04 | 50.0435 | Yes | 36
23 | 1.4 | 84 | 117.6 | 7.2 | 9.07 | 51.6796 | Yes | 36
24 | 1.3 | 84 | 109.2 | 7 | 9.05 | 51.3989 | Yes | 36
25 | 1.3 | 84 | 109.2 | 6.9 | 9.02 | 51.184 | Yes | 36
26 | 1.2 | 84 | 100.8 | 6.7 | 9 | 50.9061 | Yes | 36
27 | 1.2 | 84 | 100.8 | 6.6 | 9.01 | 51.4551 | Yes | 36
28 | 1.1 | 84 | 92.4 | 6.6 | 9.02 | 51.0322 | Yes | 36
29 | 1.2 | 84 | 100.8 | 6.6 | 9.01 | 51.4551 | Yes | 36
30 | 1.3 | 84 | 109.2 | 6.6 | 9.02 | 52.2704 | Yes | 36
31 |  | 84 | [5 empty] | 36
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised October 2013
PAGE 2 of 2