## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Linn
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2024-01-01
System Name: | Big Lake Youth Camp |  |  | ID#: 41 | 90958 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 4 | 8 | -4 | 30 | 0.09 | 0.09
2 | 4 | 8 | -4 | 30 | 0.08 | 0.08
3 | 4 | 8 | -4 | 30 | 0.07 | 0.07
4 | 4 | 8 | -4 | 30 | 0.07 | 0.07
5 | 6 | 8 | -2 | 30 | 0.08 | 0.08
6 | 6 | 8 | -2 | 30 | 0.08 | 0.08
7 | 6 | 8 | -2 | 30 | 0.08 | 0.08
8 | 6 | 8 | -2 | 30 | 0.08 | 0.08
9 | 6 | 8 | -2 | 30 | 0.08 | 0.08
10 | 6 | 8 | -2 | 30 | 0.08 | 0.08
11 | 8 | 10 | -2 | 30 | 0.09 | 0.09
12 | 8 | 10 | -2 | 30 | 0.09 | 0.09
13 | 8 | 10 | -2 | 30 | 0.09 | 0.09
14 | 8 | 10 | -2 | 30 | 0.09 | 0.09
15 | 8 | 10 | -2 | 30 | 0.1 | 0.1
16 | 8 | 10 | -2 | 30 | 0.1 | 0.1
17 | 8 | 10 | -2 | 30 | 0.1 | 0.1
18 | 8 | 10 | -2 | 30 | 0.1 | 0.1
19 | 9 | 10 | -1 | 30 | 0.09 | 0.09
20 | 9 | 10 | -1 | 30 | 0.09 | 0.09
21 | 10 | 11 | -1 | 30 | 0.09 | 0.09
22 | 10 | 11 | -1 | 30 | 0.08 | 0.08
23 | 10 | 12 | -2 | 30 | 0.08 | 0.08
24 | 10 | 12 | -2 | 30 | 0.09 | 0.09
25 | 10 | 12 | -2 | 30 | 0.09 | 0.09
26 | 10 | 13 | -3 | 30 | 0.1 | 0.1
27 | 10 | 13 | -3 | 30 | 0.1 | 0.1
28 | 11 | 13 | -2 | 30 | 0.12 | 0.12
29 | 11 | 14 | -3 | 30 | 0.12 | 0.12
30 | 11 | 14 | -3 | 30 | 0.14 | 0.14
31 | 11 | 15 | -4 | 30 | 0.13 | 0.13
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes / No | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes / No | Yes / No | Yes / No
Notes: PSI = pounds per square inch |  |  |  |  | Printed name:Randy Stroud
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | Signature:Randy Stroud |  | 2024-01-31
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | (503)580-3576 |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Big Lake Youth Camp |  | ID#: 41 | 90958 | Month/Year: |  | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 3.7 | 84 | 310.8 | 1.9 | 7.28 | 50.6056 | Yes | 36
2 | 3.4 | 84 | 285.6 | 1.9 | 6.94 | 43.0352 | Yes | 36
3 | 2.7 | 84 | 226.8 | 1.6 | 7.12 | 43.2165 | Yes | 36
4 | 2.5 | 84 | 210 | 1.6 | 7.08 | 41.5829 | Yes | 36
5 | 2.4 | 84 | 201.6 | 1.6 | 6.99 | 39.7518 | Yes | 36
6 | 2.2 | 84 | 184.8 | 1.6 | 7.03 | 39.3983 | Yes | 36
7 | 2 | 84 | 168 | 1.6 | 7.15 | 40.2153 | Yes | 36
8 | 1.9 | 84 | 159.6 | 1.6 | 6.89 | 36.123 | Yes | 36
9 | 1.7 | 84 | 142.8 | 1.6 | 6.93 | 35.8035 | Yes | 36
10 | 1.5 | 84 | 126 | 1.6 | 7.09 | 37.0815 | Yes | 36
11 | 1.3 | 84 | 109.2 | 1.5 | 7.13 | 37.0068 | Yes | 36
12 | 1.1 | 84 | 92.4 | 1.5 | 6.92 | 33.4763 | Yes | 36
13 | 1 | 84 | 84 | 1.5 | 6.71 | 30.6576 | Yes | 36
14 | 0.9 | 84 | 75.6 | 1.5 | 6.99 | 33.5463 | Yes | 36
15 | 0.9 | 84 | 75.6 | 1.4 | 6.84 | 31.9822 | Yes | 36
16 | 0.8 | 84 | 67.2 | 1.4 | 6.78 | 30.9309 | Yes | 36
17 | 0.8 | 84 | 67.2 | 1.4 | 6.73 | 30.3759 | Yes | 36
18 | 0.7 | 84 | 58.8 | 1.4 | 6.71 | 29.8086 | Yes | 36
19 | 0.7 | 84 | 58.8 | 1.4 | 6.73 | 30.0249 | Yes | 36
20 | 0.7 | 84 | 58.8 | 1.4 | 6.76 | 30.3525 | Yes | 36
21 | 0.7 | 84 | 58.8 | 1.4 | 6.78 | 30.573 | Yes | 36
22 | 0.6 | 84 | 50.4 | 1.4 | 6.8 | 30.439 | Yes | 36
23 | 0.6 | 84 | 50.4 | 1.4 | 6.82 | 30.6602 | Yes | 36
24 | 0.6 | 84 | 50.4 | 1.4 | 6.78 | 30.2195 | Yes | 36
25 | 0.6 | 84 | 50.4 | 1.4 | 6.67 | 29.0425 | Yes | 36
26 | 0.5 | 84 | 42 | 1.4 | 6.81 | 30.1962 | Yes | 36
27 | 0.5 | 84 | 42 | 1.5 | 6.84 | 30.3192 | Yes | 36
28 | 0.5 | 84 | 42 | 1.5 | 6.74 | 29.2432 | Yes | 36
29 | 0.5 | 84 | 42 | 1.5 | 6.63 | 28.1071 | Yes | 36
30 | 0.4 | 84 | 33.6 | 1.5 | 6.56 | 27.0948 | Yes | 36
31 | 0.4 | 84 | 33.6 | 1.6 | 6.61 | 27.4001 | Yes | 36
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised October 2013
PAGE 2 of 2