## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Linn
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2024-02-01
System Name: | Big Lake Youth Camp |  |  | ID#: 41 | 90958 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 11 | 15 | -4 | 30 | 0.11 | 0.11
2 | 11 | 16 | -5 | 30 | 0.11 | 0.11
3 | 11 | 16 | -5 | 30 | 0.1 | 0.1
4 | 11 | 16 | -5 | 30 | 0.1 | 0.1
5 | 11 | 17 | -6 | 30 | 0.09 | 0.09
6 | 11 | 18 | -7 | 30 | 0.09 | 0.09
7 | 11 | 18 | -7 | 30 | 0.08 | 0.08
8 | 11 | 19 | -8 | 30 | 0.08 | 0.08
9 | 11 | 20 | -9 | 30 | 0.07 | 0.07
10 | 2 | 4 | -2 | 30 | 0.07 | 0.07
11 | 2 | 4 | -2 | 30 | 0.07 | 0.07
12 | 2 | 4 | -2 | 30 | 0.07 | 0.07
13 | 2 | 5 | -3 | 30 | 0.08 | 0.08
14 | 2 | 5 | -3 | 30 | 0.08 | 0.08
15 | 2 | 5 | -3 | 30 | 0.09 | 0.09
16 | 2 | 5 | -3 | 30 | 0.09 | 0.09
17 | 2 | 6 | -4 | 30 | 0.1 | 0.1
18 | 2 | 6 | -4 | 30 | 0.1 | 0.1
19 | 2 | 6 | -4 | 30 | 0.11 | 0.11
20 | 2 | 6 | -4 | 30 | 0.13 | 0.13
21 | 2 | 6 | -4 | 30 | 0.13 | 0.13
22 | 2 | 7 | -5 | 30 | 0.13 | 0.13
23 | 2 | 7 | -5 | 30 | 0.15 | 0.15
24 | 2 | 7 | -5 | 30 | 0.17 | 0.17
25 | 2 | 7 | -5 | 30 | 0.19 | 0.19
26 | 2 | 8 | -6 | 30 | 0.22 | 0.22
27 | 2 | 8 | -6 | 30 | 0.24 | 0.24
28 | 4 | 8 | -4 | 30 | 0.21 | 0.21
29 | 4 | 8 | -4 | 30 | 0.19 | 0.19
30 |  |  |  | 30
31 |  |  |  | 30
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME:Randy Stroud
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE:Randy Stroud |  | DATE:3/7/2024
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: ( 503 )580-3576 |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Big Lake Youth Camp |  | ID#: 41 | 90958 | Month/Year: |  | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.6 | 84 | 50.4 | 1.5 | 6.72 | 29.3716 | Yes | 36
2 | 0.7 | 84 | 58.8 | 1.5 | 6.77 | 30.2563 | Yes | 36
3 | 0.7 | 84 | 58.8 | 1.4 | 6.81 | 30.907 | Yes | 36
4 | 0.7 | 84 | 58.8 | 1.4 | 6.85 | 31.3584 | Yes | 36
5 | 0.9 | 84 | 75.6 | 1.5 | 6.8 | 31.3073 | Yes | 36
6 | 0.9 | 84 | 75.6 | 1.5 | 6.79 | 31.194 | Yes | 36
7 | 1 | 84 | 84 | 1.6 | 6.81 | 31.5738 | Yes | 36
8 | 1 | 84 | 84 | 1.6 | 6.83 | 31.8039 | Yes | 36
9 | 1 | 84 | 84 | 1.5 | 6.86 | 32.3724 | Yes | 36
10 | 1.3 | 84 | 109.2 | 1.5 | 6.84 | 33.285 | Yes | 36
11 | 1.3 | 84 | 109.2 | 1.5 | 6.87 | 33.6508 | Yes | 36
12 | 1.3 | 84 | 109.2 | 1.5 | 6.85 | 33.4065 | Yes | 36
13 | 1.4 | 84 | 117.6 | 1.4 | 6.83 | 33.7848 | Yes | 36
14 | 1.5 | 84 | 126 | 1.4 | 6.81 | 33.9346 | Yes | 36
15 | 1.5 | 84 | 126 | 1.4 | 6.89 | 34.9403 | Yes | 36
16 | 1.7 | 84 | 142.8 | 1.5 | 6.87 | 35.2675 | Yes | 36
17 | 1.7 | 84 | 142.8 | 1.5 | 6.86 | 35.1388 | Yes | 36
18 | 1.7 | 84 | 142.8 | 1.6 | 6.88 | 35.1547 | Yes | 36
19 | 1.8 | 84 | 151.2 | 1.6 | 6.85 | 35.1821 | Yes | 36
20 | 1.9 | 84 | 159.6 | 1.5 | 6.82 | 35.452 | Yes | 36
21 | 1.9 | 84 | 159.6 | 1.5 | 6.8 | 35.1937 | Yes | 36
22 | 2 | 84 | 168 | 1.5 | 6.78 | 35.3501 | Yes | 36
23 | 2 | 84 | 168 | 1.4 | 6.81 | 35.9866 | Yes | 36
24 | 2 | 84 | 168 | 1.4 | 6.83 | 36.2511 | Yes | 36
25 | 2.1 | 84 | 176.4 | 1.4 | 6.82 | 36.5462 | Yes | 36
26 | 2.1 | 84 | 176.4 | 1.4 | 6.85 | 36.9503 | Yes | 36
27 | 2.1 | 84 | 176.4 | 1.4 | 6.84 | 36.8151 | Yes | 36
28 | 1.9 | 84 | 159.6 | 1.4 | 6.83 | 35.8271 | Yes | 36
29 | 1.9 | 84 | 159.6 | 1.4 | 6.8 | 35.436 | Yes | 36
30 |  | 84 | [5 empty] | 36
31 |  | 84 | [5 empty] | 36
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised October 2013
PAGE 2 of 2