## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Linn
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2024-03-01
System Name: | Big Lake Youth Camp |  |  | ID#: 41 | 90958 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 6 | 8 | -2 | 30 | 0.19 | 0.19
2 | 6 | 8 | -2 | 30 | 0.18 | 0.18
3 | 6 | 8 | -2 | 30 | 0.18 | 0.18
4 | 6 | 9 | -3 | 30 | 0.17 | 0.17
5 | 7 | 9 | -2 | 30 | 0.17 | 0.17
6 | 7 | 9 | -2 | 30 | 0.16 | 0.16
7 | 7 | 9 | -2 | 30 | 0.15 | 0.15
8 | 7 | 9 | -2 | 30 | 0.15 | 0.15
9 | 8 | 10 | -2 | 30 | 0.14 | 0.14
10 | 8 | 10 | -2 | 30 | 0.13 | 0.13
11 | 8 | 10 | -2 | 30 | 0.12 | 0.12
12 | 8 | 10 | -2 | 30 | 0.12 | 0.12
13 | 9 | 11 | -2 | 30 | 0.11 | 0.11
14 | 9 | 11 | -2 | 30 | 0.11 | 0.11
15 | 9 | 11 | -2 | 30 | 0.11 | 0.11
16 | 9 | 11 | -2 | 30 | 0.11 | 0.11
17 | 9 | 11 | -2 | 30 | 0.12 | 0.12
18 | 10 | 12 | -2 | 30 | 0.12 | 0.12
19 | 10 | 12 | -2 | 30 | 0.12 | 0.12
20 | 10 | 12 | -2 | 30 | 0.12 | 0.12
21 | 12 | 12 | 0 | 30 | 0.13 | 0.13
22 | 12 | 14 | -2 | 30 | 0.12 | 0.12
23 | 12 | 14 | -2 | 30 | 0.12 | 0.12
24 | 12 | 14 | -2 | 30 | 0.11 | 0.11
25 | 12 | 15 | -3 | 30 | 0.11 | 0.11
26 | 12 | 15 | -3 | 30 | 0.1 | 0.1
27 | 12 | 15 | -3 | 30 | 0.1 | 0.1
28 | 12 | 17 | -5 | 30 | 0.1 | 0.1
29 | 12 | 17 | -5 | 30 | 0.09 | 0.09
30 | 12 | 17 | -5 | 30 | 0.09 | 0.09
31 | 12 | 19 | -7 | 30 | 0.09 | 0.09
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME:Randy Stroud
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE:Randy Stroud |  | DATE:4/8/2024
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #:(503)850-3576 |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Big Lake Youth Camp |  | ID#: 41 | 90958 | Month/Year: | 2024-03-01 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.9 | 84 | 159.6 | 1.4 | 6.8 | 35.436 | Yes | 36
2 | 1.8 | 84 | 151.2 | 1.4 | 6.78 | 34.7671 | Yes | 36
3 | 1.8 | 84 | 151.2 | 1.4 | 6.76 | 34.5141 | Yes | 36
4 | 1.7 | 84 | 142.8 | 1.4 | 6.79 | 34.4872 | Yes | 36
5 | 1.7 | 84 | 142.8 | 1.4 | 6.83 | 34.9948 | Yes | 36
6 | 1.6 | 84 | 134.4 | 1.4 | 6.81 | 34.3348 | Yes | 36
7 | 1.6 | 84 | 134.4 | 1.4 | 6.73 | 33.3477 | Yes | 36
8 | 1.5 | 84 | 126 | 1.4 | 6.77 | 33.4434 | Yes | 36
9 | 1.5 | 84 | 126 | 1.4 | 6.82 | 34.0586 | Yes | 36
10 | 1.4 | 84 | 117.6 | 1.4 | 6.79 | 33.2959 | Yes | 36
11 | 1.3 | 84 | 109.2 | 1.4 | 6.76 | 32.5514 | Yes | 36
12 | 1.3 | 84 | 109.2 | 1.4 | 6.73 | 32.1983 | Yes | 36
13 | 1.2 | 84 | 100.8 | 1.4 | 6.71 | 31.5944 | Yes | 36
14 | 1.2 | 84 | 100.8 | 1.5 | 6.75 | 31.8389 | Yes | 36
15 | 1.2 | 84 | 100.8 | 1.5 | 6.78 | 32.1878 | Yes | 36
16 | 1.1 | 84 | 92.4 | 1.6 | 6.77 | 31.4838 | Yes | 36
17 | 1.1 | 84 | 92.4 | 1.6 | 6.81 | 31.9443 | Yes | 36
18 | 1 | 84 | 84 | 1.7 | 6.76 | 30.7964 | Yes | 36
19 | 1 | 84 | 84 | 1.7 | 6.74 | 30.5741 | Yes | 36
20 | 1 | 84 | 84 | 1.8 | 6.71 | 30.0394 | Yes | 36
21 | 0.9 | 84 | 75.6 | 1.9 | 6.7 | 29.3857 | Yes | 36
22 | 0.9 | 84 | 75.6 | 1.9 | 6.72 | 29.5987 | Yes | 36
23 | 0.9 | 84 | 75.6 | 1.8 | 6.73 | 29.9079 | Yes | 36
24 | 0.9 | 84 | 75.6 | 1.8 | 6.77 | 30.3437 | Yes | 36
25 | 0.9 | 84 | 75.6 | 1.7 | 6.76 | 30.4401 | Yes | 36
26 | 0.8 | 84 | 67.2 | 1.7 | 6.81 | 30.6376 | Yes | 36
27 | 0.8 | 84 | 67.2 | 1.7 | 6.83 | 30.8604 | Yes | 36
28 | 0.8 | 84 | 67.2 | 1.6 | 6.8 | 30.735 | Yes | 36
29 | 0.8 | 84 | 67.2 | 1.6 | 6.78 | 30.5133 | Yes | 36
30 | 0.7 | 84 | 58.8 | 1.6 | 6.75 | 29.8352 | Yes | 36
31 | 0.7 | 84 | 58.8 | 1.5 | 6.77 | 30.2563 | Yes | 36
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised October 2013
PAGE 2 of 2