## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Linn
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2024-04-01
System Name: | Big Lake Youth Camp |  |  | ID#: 41 | 90958 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 12 | 15 | -3 | 30 | 0.09 | 0.09
2 | 12 | 16 | -4 | 30 | 0.09 | 0.09
3 | 12 | 16 | -4 | 30 | 0.09 | 0.09
4 | 12 | 17 | -5 | 30 | 0.08 | 0.08
5 | 12 | 17 | -5 | 30 | 0.08 | 0.08
6 | 12 | 18 | -6 | 30 | 0.08 | 0.08
7 | 12 | 18 | -6 | 30 | 0.08 | 0.08
8 | 12 | 20 | -8 | 30 | 0.08 | 0.08
9 | 12 | 20 | -8 | 30 | 0.09 | 0.09
10 | 12 | 20 | -8 | 30 | 0.09 | 0.09
11 | 12 | 22 | -10 | 30 | 0.09 | 0.09
12 | 12 | 22 | -10 | 30 | 0.09 | 0.09
13 | 12 | 22 | -10 | 30 | 0.09 | 0.09
14 | 14 | 22 | -8 | 30 | 0.09 | 0.09
15 | 14 | 24 | -10 | 30 | 0.09 | 0.09
16 | 14 | 24 | -10 | 30 | 0.09 | 0.09
17 | 14 | 24 | -10 | 30 | 0.09 | 0.09
18 | 14 | 26 | -12 | 30 | 0.1 | 0.1
19 | 14 | 26 | -12 | 30 | 0.1 | 0.1
20 | 16 | 28 | -12 | 30 | 0.1 | 0.1
21 | 16 | 28 | -12 | 30 | 0.1 | 0.1
22 | 16 | 28 | -12 | 30 | 0.09 | 0.09
23 | 16 | 30 | -14 | 30 | 0.09 | 0.09
24 | 16 | 30 | -14 | 30 | 0.09 | 0.09
25 | 16 | 30 | -14 | 30 | 0.1 | 0.1
26 | 16 | 32 | -16 | 30 | 0.1 | 0.1
27 | 16 | 32 | -16 | 30 | 0.1 | 0.1
28 | 16 | 32 | -16 | 30 | 0.1 | 0.1
29 | 16 | 34 | -18 | 30 | 0.1 | 0.1
30 | 4 | 8 | -4 | 30 | 0.12 | 0.12
31 | 4 | 8 | -4 | 30 | 0.12 | 0.12
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME:Randy Stroud
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE:Randy Stroud |  | DATE:5/9/2024
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: (503) 850-3576 |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Big Lake Youth Camp |  | ID#: 41 | 90958 | Month/Year: |  | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.7 | 84 | 58.8 | 1.5 | 6.77 | 30.2563 | Yes | 36
2 | 0.7 | 84 | 58.8 | 1.5 | 6.74 | 29.9299 | Yes | 36
3 | 0.7 | 84 | 58.8 | 1.4 | 6.79 | 30.6839 | Yes | 36
4 | 0.7 | 84 | 58.8 | 1.4 | 6.82 | 31.0192 | Yes | 36
5 | 0.6 | 84 | 50.4 | 1.4 | 6.8 | 30.439 | Yes | 36
6 | 0.6 | 84 | 50.4 | 1.5 | 6.78 | 30.0151 | Yes | 36
7 | 0.6 | 84 | 50.4 | 1.4 | 6.75 | 29.8935 | Yes | 36
8 | 0.6 | 84 | 50.4 | 1.4 | 6.69 | 29.2527 | Yes | 36
9 | 0.7 | 84 | 58.8 | 1.5 | 6.68 | 29.2883 | Yes | 36
10 | 0.7 | 84 | 58.8 | 1.5 | 6.65 | 28.9731 | Yes | 36
11 | 0.7 | 84 | 58.8 | 1.5 | 6.67 | 29.1828 | Yes | 36
12 | 0.8 | 84 | 67.2 | 1.5 | 6.7 | 29.8449 | Yes | 36
13 | 0.8 | 84 | 67.2 | 1.6 | 6.68 | 29.43 | Yes | 36
14 | 0.8 | 84 | 67.2 | 1.6 | 6.72 | 29.8582 | Yes | 36
15 | 0.9 | 84 | 75.6 | 1.6 | 6.75 | 30.5369 | Yes | 36
16 | 0.9 | 84 | 75.6 | 1.6 | 6.73 | 30.3166 | Yes | 36
17 | 0.9 | 84 | 75.6 | 1.5 | 6.69 | 30.0847 | Yes | 36
18 | 0.9 | 84 | 75.6 | 1.5 | 6.64 | 29.546 | Yes | 36
19 | 0.9 | 84 | 75.6 | 1.6 | 6.68 | 29.7735 | Yes | 36
20 | 0.9 | 84 | 75.6 | 1.6 | 6.71 | 30.0981 | Yes | 36
21 | 1 | 84 | 84 | 1.6 | 6.73 | 30.6713 | Yes | 36
22 | 1 | 84 | 84 | 1.6 | 6.7 | 30.34 | Yes | 36
23 | 1 | 84 | 84 | 1.6 | 6.69 | 30.2305 | Yes | 36
24 | 1 | 84 | 84 | 1.6 | 6.72 | 30.5605 | Yes | 36
25 | 1 | 84 | 84 | 1.6 | 6.68 | 30.1213 | Yes | 36
26 | 1.1 | 84 | 92.4 | 1.6 | 6.66 | 30.2538 | Yes | 36
27 | 1.1 | 84 | 92.4 | 1.6 | 6.67 | 30.3635 | Yes | 36
28 | 1.1 | 84 | 92.4 | 1.5 | 6.73 | 31.2423 | Yes | 36
29 | 1.1 | 84 | 92.4 | 1.5 | 6.71 | 31.0166 | Yes | 36
30 | 1.2 | 84 | 100.8 | 1.5 | 6.69 | 31.1533 | Yes | 36
31 | 1.2 | 84 | 100.8 | 1.5 | 6.72 | 31.4941 | Yes | 36
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised October 2013
PAGE 2 of 2