## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Linn
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2024-05-01
System Name: | Big Lake Youth Camp |  |  | ID#: 41 | 90958 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 6 | 1 | 5 | 30 | 0.09 | 0.09
2 | 6 | 1 | 5 | 30 | 0.09 | 0.09
3 | 6 | 1 | 5 | 30 | 0.09 | 0.09
4 | 6 | 1 | 5 | 30 | 0.09 | 0.09
5 | 6 | 1 | 5 | 30 | 0.09 | 0.09
6 | 6 | 1 | 5 | 30 | 0.09 | 0.09
7 | 6 | 1 | 5 | 30 | 0.1 | 0.1
8 | 6 | 1 | 5 | 30 | 0.1 | 0.1
9 | 6 | 1 | 5 | 30 | 0.1 | 0.1
10 | 6 | 1 | 5 | 30 | 0.1 | 0.1
11 | 6 | 1 | 5 | 30 | 0.12 | 0.12
12 | 6 | 1 | 5 | 30 | 0.12 | 0.12
13 | 6 | 1 | 5 | 30 | 0.12 | 0.12
14 | 6 | 1 | 5 | 30 | 0.13 | 0.13
15 | 6 | 1 | 5 | 30 | 0.13 | 0.13
16 | 8 | 2 | 6 | 30 | 0.15 | 0.15
17 | 8 | 2 | 6 | 30 | 0.17 | 0.17
18 | 8 | 2 | 6 | 30 | 0.19 | 0.19
19 | 8 | 2 | 6 | 30 | 0.21 | 0.21
20 | 8 | 2 | 6 | 30 | 0.24 | 0.24
21 | 8 | 2 | 6 | 30 | 0.27 | 0.27
22 | 8 | 2 | 6 | 30 | 0.31 | 0.31
23 | 8 | 2 | 6 | 30 | 0.34 | 0.34
24 | 8 | 2 | 6 | 30 | 0.36 | 0.36
25 | 8 | 2 | 6 | 30 | 0.36 | 0.36
26 | 8 | 2 | 6 | 30 | 0.4 | 0.4
27 | 8 | 2 | 6 | 30 | 0.47 | 0.47
28 | 8 | 2 | 6 | 30 | 0.5 | 0.5
29 | 8 | 2 | 6 | 30 | 0.53 | 0.53
30 | 8 | 2 | 6 | 30 | 0.56 | 0.56
31 | 8 | 2 | 6 | 30 | 0.6 | 0.6
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME:Randy Stroud
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE:Randy Stroud |  | DATE:6/6/2024
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: (503)850-3576 |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Big Lake Youth Camp |  | ID#: 41 | 90958 | Month/Year: |  | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.2 | 84 | 100.8 | 1.6 | 6.68 | 30.8302 | Yes | 36
2 | 1.2 | 84 | 100.8 | 1.6 | 6.7 | 31.0545 | Yes | 36
3 | 1.2 | 84 | 100.8 | 1.6 | 6.73 | 31.3941 | Yes | 36
4 | 1.2 | 84 | 100.8 | 1.6 | 6.71 | 31.1672 | Yes | 36
5 | 1.2 | 84 | 100.8 | 1.6 | 6.74 | 31.5082 | Yes | 36
6 | 1.1 | 84 | 92.4 | 1.6 | 6.75 | 31.2563 | Yes | 36
7 | 1.1 | 84 | 92.4 | 1.7 | 6.77 | 31.2702 | Yes | 36
8 | 1.1 | 84 | 92.4 | 1.7 | 6.79 | 31.4979 | Yes | 36
9 | 1.1 | 84 | 92.4 | 1.8 | 6.76 | 30.9459 | Yes | 36
10 | 1.1 | 84 | 92.4 | 1.8 | 6.8 | 31.3979 | Yes | 36
11 | 1.1 | 84 | 92.4 | 1.9 | 6.82 | 31.412 | Yes | 36
12 | 1.1 | 84 | 92.4 | 1.9 | 6.85 | 31.7558 | Yes | 36
13 | 1.1 | 84 | 92.4 | 2 | 6.87 | 31.7701 | Yes | 36
14 | 1.1 | 84 | 92.4 | 2.1 | 6.91 | 32.016 | Yes | 36
15 | 1.1 | 84 | 92.4 | 2.2 | 6.9 | 31.6833 | Yes | 36
16 | 1.1 | 84 | 92.4 | 2.3 | 6.93 | 31.8128 | Yes | 36
17 | 1.1 | 84 | 92.4 | 2.4 | 6.95 | 31.827 | Yes | 36
18 | 1.1 | 84 | 92.4 | 2.4 | 6.97 | 32.0591 | Yes | 36
19 | 1.1 | 84 | 92.4 | 2.5 | 6.99 | 32.0734 | Yes | 36
20 | 1.1 | 84 | 92.4 | 2.6 | 6.98 | 31.7401 | Yes | 36
21 | 1 | 84 | 84 | 2.7 | 7 | 31.3862 | Yes | 36
22 | 1 | 84 | 84 | 2.8 | 7.01 | 31.2866 | Yes | 36
23 | 1 | 84 | 84 | 3 | 7.04 | 31.2012 | Yes | 36
24 | 1 | 84 | 84 | 3.3 | 7.07 | 30.9052 | Yes | 36
25 | 1 | 84 | 84 | 3.6 | 7.08 | 30.3914 | Yes | 36
26 | 1 | 84 | 84 | 3.8 | 7.06 | 29.7657 | Yes | 36
27 | 1 | 84 | 84 | 4 | 7.09 | 29.6849 | Yes | 36
28 | 1 | 84 | 84 | 4.4 | 7.04 | 28.3759 | Yes | 36
29 | 1 | 84 | 84 | 4.7 | 7.05 | 27.9072 | Yes | 36
30 | 1 | 84 | 84 | 4.7 | 7.03 | 27.7074 | Yes | 36
31 | 1 | 84 | 84 | 4.9 | 7.07 | 27.7319 | Yes | 36
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised October 2013
PAGE 2 of 2