## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Linn
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2024-06-01
System Name: | Big Lake Youth Camp |  |  | ID#: 41 | 90958 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 2 | 8 | -6 | 30 | 0.93 | 0.93
2 | 2 | 8 | -6 | 30 | 0.96 | 0.96
3 | 2 | 8 | -6 | 30 | 0.98 | 0.98
4 | 2 | 8 | -6 | 30 | 1.01 | 1.01
5 | 2 | 8 | -6 | 30 | 1.05 | 1.05
6 | 2 | 8 | -6 | 30 | 1.08 | 1.08
7 | 2 | 8 | -6 | 30 | 0.55 | 0.55
8 | 2 | 8 | -6 | 30 | 0.22 | 0.22
9 | 2 | 8 | -6 | 30 | 0.07 | 0.07
10 | 2 | 8 | -6 | 30 | 0.9 | 0.9
11 | 2 | 8 | -6 | 30 | 0.57 | 0.57
12 | 2 | 8 | -6 | 30 | 0.42 | 0.42
13 | 4 | 10 | -6 | 30 | 0.37 | 0.37
14 | 4 | 10 | -6 | 30 | 0.33 | 0.33
15 | 4 | 10 | -6 | 30 | 0.3 | 0.3
16 | 4 | 12 | -8 | 30 | 0.25 | 0.25
17 | 4 | 12 | -8 | 30 | 0.32 | 0.32
18 | 4 | 12 | -8 | 30 | 0.39 | 0.39
19 | 6 | 14 | -8 | 30 | 0.45 | 0.45
20 | 6 | 14 | -8 | 30 | 0.48 | 0.48
21 | 6 | 14 | -8 | 30 | 0.51 | 0.51
22 | 6 | 16 | -10 | 30 | 0.46 | 0.46
23 | 6 | 16 | -10 | 30 | 0.41 | 0.41
24 | 6 | 16 | -10 | 30 | 0.37 | 0.37
25 | 6 | 16 | -10 | 30 | 0.32 | 0.32
26 | 8 | 16 | -8 | 30 | 0.26 | 0.26
27 | 8 | 18 | -10 | 30 | 0.29 | 0.29
28 | 8 | 18 | -10 | 30 | 0.24 | 0.24
29 | 8 | 18 | -10 | 30 | 0.17 | 0.17
30 | 8 | 18 | -10 | 30 | 0.12 | 0.12
31 |  |  |  | 30
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME:Randy Stroud
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE:Randy Stroud |  | DATE:7/9/2024
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: ( 218)330-3836 |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Big Lake Youth Camp |  | ID#: 41 | 90958 | Month/Year: |  | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1 | 84 | 84 | 5.1 | 7.09 | 27.5579 |  | 36
2 | 1 | 84 | 84 | 5.4 | 7.11 | 27.2012 |  | 36
3 | 1 | 84 | 84 | 5.7 | 7.13 | 26.8495 |  | 36
4 | 1 | 84 | 84 | 6 | 7.1 | 26.0331 |  | 36
5 | 1 | 84 | 84 | 6.3 | 7.13 | 25.7897 |  | 36
6 | 1 | 84 | 84 | 6.7 | 7.17 | 25.469 |  | 36
7 | 1.4 | 84 | 117.6 | 8 | 7.19 | 24.6182 |  | 36
8 | 1.2 | 84 | 100.8 | 8.8 | 7.25 | 23.3066 |  | 36
9 | 3.5 | 84 | 294 | 9.6 | 7.8 | 35.1177 |  | 36
10 | 2.2 | 84 | 184.8 | 9.8 | 7.6 | 27.6928 |  | 36
11 | 1.9 | 84 | 159.6 | 9.7 | 7.55 | 26.4541 |  | 36
12 | 1.6 | 84 | 134.4 | 9.6 | 7.5 | 25.2753 |  | 36
13 | 1.4 | 84 | 117.6 | 10 | 7.45 | 23.6312 |  | 36
14 | 1.4 | 84 | 117.6 | 10.3 | 7.42 | 22.921 |  | 36
15 | 1.3 | 84 | 109.2 | 10.6 | 7.38 | 21.9073 |  | 36
16 | 1.3 | 84 | 109.2 | 10.9 | 7.35 | 21.254 |  | 36
17 | 1.3 | 84 | 109.2 | 11.2 | 7.24 | 20.0553 |  | 36
18 | 1.2 | 84 | 100.8 | 11.5 | 7.21 | 19.2478 |  | 36
19 | 1.2 | 84 | 100.8 | 11.9 | 7.16 | 18.4344 |  | 36
20 | 1.2 | 84 | 100.8 | 12.1 | 7.09 | 17.766 |  | 36
21 | 1.1 | 84 | 92.4 | 12.3 | 7.12 | 17.5264 |  | 36
22 | 1.1 | 84 | 92.4 | 12.7 | 7.23 | 17.4884 |  | 36
23 | 1.1 | 84 | 92.4 | 13 | 7.19 | 16.8912 |  | 36
24 | 1.1 | 84 | 92.4 | 13.4 | 7.14 | 16.1457 |  | 36
25 | 1 | 84 | 84 | 13.6 | 7.11 | 15.5774 |  | 36
26 | 1 | 84 | 84 | 13.9 | 7.07 | 15.044 |  | 36
27 | 1 | 84 | 84 | 14.2 | 7.03 | 14.5284 |  | 36
28 | 0.9 | 84 | 75.6 | 14.5 | 6.9 | 13.4141 |  | 36
29 | 0.9 | 84 | 75.6 | 14.8 | 6.87 | 13.0011 |  | 36
30 | 0.9 | 84 | 75.6 | 15.1 | 6.84 | 12.6006 |  | 36
31 |  | 84 | [5 empty] | 36
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised October 2013
PAGE 2 of 2