## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Linn
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2024-07-01
System Name: | Big Lake Youth Camp |  |  | ID#: 41 | 90958 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 8 | 18 | -10 | 30 | 0.12 | 0.12
2 | 8 | 18 | -10 | 30 | 0.14 | 0.14
3 | 8 | 18 | -10 | 30 | 0.15 | 0.15
4 | 8 | 18 | -10 | 30 | 0.16 | 0.16
5 | 8 | 18 | -10 | 30 | 0.18 | 0.18
6 | 8 | 18 | -10 | 30 | 0.21 | 0.21
7 | 8 | 20 | -12 | 30 | 0.24 | 0.24
8 | 8 | 20 | -12 | 30 | 0.27 | 0.27
9 | 8 | 20 | -12 | 30 | 0.29 | 0.29
10 | 7 | 19 | -12 | 30 | 1.05 | 1.05
11 | 7 | 19 | -12 | 30 | 0.73 | 0.73
12 | 7 | 19 | -12 | 30 | 0.76 | 0.76
13 | 7 | 19 | -12 | 30 | 0.8 | 0.8
14 | 7 | 19 | -12 | 30 | 0.75 | 0.75
15 | 7 | 19 | -12 | 30 | 0.9 | 0.9
16 | 7 | 19 | -12 | 30 | 0.9 | 0.9
17 | 10 | 40 | -30 | 30 | 0.96 | 0.96
18 | 4 | 17 | -13 | 30 | 0.62 | 0.62
19 | 4 | 17 | -13 | 30 | 0.7 | 0.7
20 | 4 | 17 | -13 | 30 | 0.94 | 0.94
21 | 4 | 17 | -13 | 30 | 1.2 | 1.2
22 | 4 | 17 | -13 | 30 | 0.53 | 0.53
23 | 4 | 17 | -13 | 30 | 0.27 | 0.27
24 | 4 | 17 | -13 | 30 | 0.27 | 0.27
25 | 4 | 17 | -13 | 30 | 0.64 | 0.64
26 | 4 | 17 | -13 | 30 | 0.82 | 0.82
27 | 4 | 17 | -13 | 30 | 0.75 | 0.75
28 | 4 | 17 | -13 | 30 | 0.91 | 0.91
29 | 4 | 17 | -13 | 30 | 0.6 | 0.6
30 | 4 | 17 | -13 | 30 | 0.53 | 0.53
31 | 4 | 17 | -13 | 30 | 0.22 | 0.22
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME:Randy Stroud
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE:Randy Stroud |  | DATE:8/2/2024
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: (503)850-3576 |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Big Lake Youth Camp |  | ID#: 41 | 90958 | Month/Year: |  | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1 | 84 | 84 | 13.6 | 7.21 | 16.1651 | Yes | 36
2 | 0.9 | 84 | 75.6 | 14.1 | 7.18 | 15.2871 | Yes | 36
3 | 0.9 | 84 | 75.6 | 14.5 | 7.15 | 14.7196 | Yes | 36
4 | 0.9 | 84 | 75.6 | 14.8 | 7.12 | 14.2676 | Yes | 36
5 | 0.9 | 84 | 75.6 | 15 | 7.07 | 13.8189 | Yes | 36
6 | 0.8 | 84 | 67.2 | 15.5 | 6.9 | 12.4012 | Yes | 36
7 | 0.8 | 84 | 67.2 | 15.7 | 7.05 | 12.9393 | Yes | 36
8 | 0.8 | 84 | 67.2 | 16.3 | 7.08 | 12.5686 | Yes | 36
9 | 0.8 | 84 | 67.2 | 16.7 | 7.11 | 12.3732 | Yes | 36
10 | 2.4 | 84 | 201.6 | 17.3 | 7.44 | 16.1308 | Yes | 36
11 | 2.1 | 84 | 176.4 | 17.5 | 8.05 | 19.2723 | Yes | 36
12 | 2 | 84 | 168 | 17.5 | 7.6 | 16.1367 | Yes | 36
13 | 1.8 | 84 | 151.2 | 17.3 | 7.17 | 13.6282 | Yes | 36
14 | 1.8 | 84 | 151.2 | 17.5 | 7.17 | 13.4469 | Yes | 36
15 | 1.8 | 84 | 151.2 | 17.5 | 7.3 | 14.1126 | Yes | 36
16 | 1.7 | 84 | 142.8 | 18.1 | 7.22 | 13.0099 | Yes | 36
17 | 1.7 | 84 | 142.8 | 18.5 | 6.93 | 11.366 | Yes | 36
18 | 1.7 | 84 | 142.8 | 18.4 | 6.94 | 11.4857 | Yes | 36
19 | 1.6 | 84 | 134.4 | 18.4 | 7.15 | 12.2808 | Yes | 36
20 | 1.6 | 84 | 134.4 | 18.5 | 7.19 | 12.3819 | Yes | 36
21 | 1.5 | 84 | 126 | 18.5 | 7.24 | 12.4711 | Yes | 36
22 | 1.5 | 84 | 126 | 18.3 | 7.27 | 12.7817 | Yes | 36
23 | 1.3 | 84 | 109.2 | 18.2 | 7.25 | 12.4828 | Yes | 36
24 | 1.3 | 84 | 109.2 | 17.9 | 7.55 | 14.2402 | Yes | 36
25 | 1.3 | 84 | 109.2 | 17.8 | 7.84 | 15.963 | Yes | 36
26 | 1.2 | 84 | 100.8 | 17.5 | 7.81 | 15.9232 | Yes | 36
27 | 1.2 | 84 | 100.8 | 17.5 | 7.84 | 16.1011 | Yes | 36
28 | 1.2 | 84 | 100.8 | 17.5 | 7.86 | 16.2207 | Yes | 36
29 | 1.2 | 84 | 100.8 | 17.3 | 7.75 | 15.7824 | Yes | 36
30 | 1.1 | 84 | 92.4 | 17.3 | 7.71 | 15.3741 | Yes | 36
31 | 1.1 | 84 | 92.4 | 17.5 | 7.46 | 13.8259 | Yes | 36
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised October 2013
PAGE 2 of 2