## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Linn
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2024-08-01
System Name: | Big Lake Youth Camp |  |  | ID#: 41 | 90958 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 6 | 18 | -12 | 30 | 0.32 | 0.32
2 | 6 | 18 | -12 | 30 | 0.32 | 0.32
3 | 6 | 18 | -12 | 30 | 0.42 | 0.42
4 | 2 | 8 | -6 | 30 | 0.63 | 0.63
5 | 2 | 8 | -6 | 30 | 0.5 | 0.5
6 | 2 | 10 | -8 | 30 | 0.5 | 0.5
7 | 4 | 16 | -12 | 30 | 0.56 | 0.56
8 | 4 | 17 | -13 | 30 | 0.43 | 0.43
9 | 4 | 19 | -15 | 30 | 0.65 | 0.65
10 | 4 | 19 | -15 | 30 | 0.65 | 0.65
11 | 4 | 19 | -15 | 30 | 0.54 | 0.54
12 | 4 | 19 | -15 | 30 | 0.58 | 0.58
13 | 4 | 19 | -15 | 30 | 0.56 | 0.56
14 | 8 | 20 | -12 | 30 | 0.51 | 0.51
15 | 8 | 20 | -12 | 30 | 0.25 | 0.25
16 | 8 | 20 | -12 | 30 | 0.43 | 0.43
17 | 8 | 20 | -12 | 30 | 0.43 | 0.43
18 | 8 | 20 | -12 | 30 | 0.44 | 0.44
19 | 8 | 22 | -14 | 30 | 0.49 | 0.49
20 | 8 | 22 | -14 | 30 | 0.52 | 0.52
21 | 8 | 22 | -14 | 30 | 0.55 | 0.55
22 | 8 | 24 | -16 | 30 | 0.57 | 0.57
23 | 8 | 24 | -16 | 30 | 0.48 | 0.48
24 | 8 | 24 | -16 | 30 | 0.43 | 0.43
25 | 2 | 8 | -6 | 30 | 0.41 | 0.41
26 | 2 | 8 | -6 | 30 | 0.46 | 0.46
27 | 2 | 8 | -6 | 30 | 0.5 | 0.5
28 | 4 | 10 | -6 | 30 | 0.47 | 0.47
29 | 4 | 10 | -6 | 30 | 0.45 | 0.45
30 | 4 | 10 | -6 | 30 | 0.42 | 0.42
31 | 4 | 12 | -8 | 30 | 0.39 | 0.39
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME:Randy Stroud
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE:Randy Stroud |  | DATE:9/9/2024
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: (503)850-3576 |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Big Lake Youth Camp |  | ID#: 41 | 90958 | Month/Year: | 2024-08-01 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.1 | 84 | 92.4 | 17.5 | 7.54 | 14.243 | Yes | 36
2 | 1.1 | 84 | 92.4 | 17.8 | 7.77 | 15.204 | Yes | 36
3 | 0.8 | 84 | 67.2 | 17.8 | 7.82 | 14.9677 | Yes | 36
4 | 0.8 | 84 | 67.2 | 17.9 | 7.76 | 14.5408 | Yes | 36
5 | 0.6 | 84 | 50.4 | 17.5 | 7.76 | 14.5977 | Yes | 36
6 | 0.6 | 84 | 50.4 | 17.5 | 7.55 | 13.5021 | Yes | 36
7 | 0.6 | 84 | 50.4 | 18.3 | 7.45 | 12.3291 | Yes | 36
8 | 0.5 | 84 | 42 | 18.3 | 7.4 | 11.9631 | Yes | 36
9 | 0.5 | 84 | 42 | 18.5 | 7.31 | 11.413 | Yes | 36
10 | 0.5 | 84 | 42 | 18.5 | 7.12 | 10.6294 | Yes | 36
11 | 0.6 | 84 | 50.4 | 18.5 | 7.06 | 10.5134 | Yes | 36
12 | 0.6 | 84 | 50.4 | 18.2 | 7.23 | 11.4333 | Yes | 36
13 | 0.9 | 84 | 75.6 | 18 | 7.85 | 15.1056 | Yes | 36
14 | 0.9 | 84 | 75.6 | 18.1 | 7.96 | 15.6295 | Yes | 36
15 | 0.9 | 84 | 75.6 | 17 | 8.06 | 17.4514 | Yes | 36
16 | 1.1 | 84 | 92.4 | 16.5 | 8.07 | 18.5237 | Yes | 36
17 | 1 | 84 | 84 | 16.5 | 8.05 | 18.1801 | Yes | 36
18 | 0.8 | 84 | 67.2 | 16 | 8.05 | 18.3725 | Yes | 36
19 | 0.8 | 84 | 67.2 | 16.1 | 7.95 | 17.5893 | Yes | 36
20 | 0.8 | 84 | 67.2 | 15.9 | 7.91 | 17.5634 | Yes | 36
21 | 0.8 | 84 | 67.2 | 15.9 | 7.87 | 17.3057 | Yes | 36
22 | 0.7 | 84 | 58.8 | 15.7 | 7.82 | 17.0219 | Yes | 36
23 | 0.7 | 84 | 58.8 | 15.5 | 7.78 | 16.9969 | Yes | 36
24 | 0.7 | 84 | 58.8 | 15.3 | 7.75 | 17.0347 | Yes | 36
25 | 1 | 84 | 84 | 15.1 | 7.7 | 17.5344 | Yes | 36
26 | 1 | 84 | 84 | 14.8 | 7.66 | 17.6255 | Yes | 36
27 | 1 | 84 | 84 | 14.6 | 7.63 | 17.6646 | Yes | 36
28 | 0.9 | 84 | 75.6 | 14.3 | 7.65 | 17.9492 | Yes | 36
29 | 0.9 | 84 | 75.6 | 14.1 | 7.58 | 17.7253 | Yes | 36
30 | 0.9 | 84 | 75.6 | 13.9 | 7.54 | 17.6992 | Yes | 36
31 | 0.9 | 84 | 75.6 | 13.7 | 7.47 | 17.4784 | Yes | 36
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised October 2013
PAGE 2 of 2