## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Linn
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2025-05-01
System Name: | Big Lake Youth Camp |  |  | ID#: 41 | 90958 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 8 | 19 | -11 | 30 | 0.19 | 0.19
2 | 8 | 19 | -11 | 30 | 0.18 | 0.18
3 | 8 | 19 | -11 | 30 | 0.17 | 0.17
4 | 8 | 19 | -11 | 30 | 0.16 | 0.16
5 | 8 | 19 | -11 | 30 | 0.16 | 0.16
6 | 8 | 19 | -11 | 30 | 0.16 | 0.16
7 | 8 | 19 | -11 | 30 | 0.15 | 0.15
8 | 8 | 19 | -11 | 30 | 0.15 | 0.15
9 | 8 | 19 | -11 | 30 | 0.14 | 0.14
10 | 8 | 19 | -11 | 30 | 0.14 | 0.14
11 | 8 | 19 | -11 | 30 | 0.13 | 0.13
12 | 9 | 19 | -10 | 30 | 0.13 | 0.13
13 | 9 | 20 | -11 | 30 | 0.13 | 0.13
14 | 9 | 20 | -11 | 30 | 0.14 | 0.14
15 | 9 | 20 | -11 | 30 | 0.14 | 0.14
16 | 9 | 20 | -11 | 30 | 0.14 | 0.14
17 | 9 | 20 | -11 | 30 | 0.15 | 0.15
18 | 9 | 20 | -11 | 30 | 0.15 | 0.15
19 | 9 | 20 | -11 | 30 | 0.16 | 0.16
20 | 9 | 20 | -11 | 30 | 0.16 | 0.16
21 | 9 | 20 | -11 | 30 | 0.16 | 0.16
22 | 9 | 20 | -11 | 30 | 0.17 | 0.17
23 | 9 | 20 | -11 | 30 | 0.17 | 0.17
24 | 9 | 20 | -11 | 30 | 0.17 | 0.17
25 | 9 | 20 | -11 | 30 | 0.18 | 0.18
26 | 9 | 20 | -11 | 30 | 0.18 | 0.18
27 | 9 | 20 | -11 | 30 | 0.18 | 0.18
28 | 9 | 20 | -11 | 30 | 0.17 | 0.1
29 | 9 | 20 | -11 | 30 | 0.17 | 0.17
30 | 9 | 20 | -11 | 30 | 0.18 | 0.18
31 | 9 | 20 | -11 | 30 | 0.19 | 0.19
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME:Randy Stroud
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE:Randy Stroud |  | DATE:6/2/2025
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: (503 )850-3576 |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Big Lake Youth Camp |  | ID#: 41 | 90958 | Month/Year: | 2025-05-01 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.4 | 84 | 117.6 | 1.9 | 7.2 | 37.3761 | Yes | 36
2 | 1.3 | 84 | 109.2 | 1.9 | 7.22 | 37.2101 | Yes | 36
3 | 1.3 | 84 | 109.2 | 1.9 | 7.24 | 37.4842 | Yes | 36
4 | 1.3 | 84 | 109.2 | 1.9 | 7.26 | 37.7604 | Yes | 36
5 | 1.2 | 84 | 100.8 | 1.9 | 7.23 | 36.9093 | Yes | 36
6 | 1.2 | 84 | 100.8 | 2.2 | 7.25 | 36.4215 | Yes | 36
7 | 1.1 | 84 | 92.4 | 2.4 | 7.27 | 35.7651 | Yes | 36
8 | 1.1 | 84 | 92.4 | 2.6 | 7.3 | 35.6667 | Yes | 36
9 | 1.1 | 84 | 92.4 | 2.8 | 7.33 | 35.5685 | Yes | 36
10 | 1 | 84 | 84 | 3 | 7.37 | 35.1847 | Yes | 36
11 | 1 | 84 | 84 | 3.2 | 7.35 | 34.4529 | Yes | 36
12 | 3.2 | 84 | 268.8 | 3.4 | 7.31 | 43.4229 | Yes | 36
13 | 3 | 84 | 252 | 3.8 | 7.32 | 41.3963 | Yes | 36
14 | 2.9 | 84 | 243.6 | 4.1 | 7.36 | 40.6633 | Yes | 36
15 | 2.7 | 84 | 226.8 | 4.6 | 7.33 | 37.9437 | Yes | 36
16 | 2.6 | 84 | 218.4 | 4.9 | 7.34 | 36.8672 | Yes | 36
17 | 2.5 | 84 | 210 | 5.2 | 7.37 | 36.0863 | Yes | 36
18 | 2.4 | 84 | 201.6 | 5.5 | 7.39 | 35.194 | Yes | 36
19 | 2.3 | 84 | 193.2 | 5.8 | 7.41 | 34.3252 | Yes | 36
20 | 2.2 | 84 | 184.8 | 6 | 7.42 | 33.5863 | Yes | 36
21 | 2.1 | 84 | 176.4 | 6.3 | 7.45 | 32.8791 | Yes | 36
22 | 2 | 84 | 168 | 6.4 | 7.48 | 32.63 | Yes | 36
23 | 1.9 | 84 | 159.6 | 6.7 | 7.5 | 31.8285 | Yes | 36
24 | 1.8 | 84 | 151.2 | 6.9 | 7.54 | 31.4876 | Yes | 36
25 | 1.7 | 84 | 142.8 | 7.1 | 7.57 | 31.038 | Yes | 36
26 | 1.6 | 84 | 134.4 | 7.3 | 7.61 | 30.7062 | Yes | 36
27 | 1.5 | 84 | 126 | 7.5 | 7.64 | 30.2684 | Yes | 36
28 | 1.4 | 84 | 117.6 | 7.7 | 7.66 | 29.7298 | Yes | 36
29 | 1.3 | 84 | 109.2 | 7.9 | 7.68 | 29.2015 | Yes | 36
30 | 1.2 | 84 | 100.8 | 8 | 7.71 | 28.9822 | Yes | 36
31 | 1.1 | 84 | 92.4 | 7.8 | 7.74 | 29.3547 | Yes | 36
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised October 2013
PAGE 2 of 2