## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Linn
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2025-06-01
System Name: | Big Lake Youth Camp |  |  | ID#: 41 | 90958 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 9 | 20 | -11 | 30 | 0.19 | 0.19
2 | 9 | 20 | -11 | 30 | 0.21 | 0.21
3 | 9 | 20 | -11 | 30 | 0.21 | 0.21
4 | 9 | 20 | -11 | 30 | 0.22 | 0.22
5 | 9 | 20 | -11 | 30 | 0.22 | 0.22
6 | 9 | 20 | -11 | 30 | 0.22 | 0.22
7 | 10 | 20 | -10 | 30 | 0.23 | 0.23
8 | 10 | 20 | -10 | 30 | 0.23 | 0.23
9 | 10 | 20 | -10 | 30 | 0.23 | 0.23
10 | 10 | 20 | -10 | 30 | 0.24 | 0.24
11 | 10 | 21 | -11 | 30 | 0.23 | 0.23
12 | 10 | 21 | -11 | 30 | 0.21 | 0.21
13 | 10 | 21 | -11 | 30 | 0.21 | 0.21
14 | 4 | 8 | -4 | 30 | 0.19 | 0.19
15 | 4 | 8 | -4 | 30 | 0.19 | 0.19
16 | 4 | 8 | -4 | 30 | 0.18 | 0.18
17 | 4 | 8 | -4 | 30 | 0.18 | 0.18
18 | 4 | 8 | -4 | 30 | 0.16 | 0.16
19 | 4 | 9 | -5 | 30 | 0.14 | 0.14
20 | 6 | 9 | -3 | 30 | 0.14 | 0.14
21 | 6 | 9 | -3 | 30 | 0.13 | 0.13
22 | 6 | 9 | -3 | 30 | 0.12 | 0.12
23 | 6 | 9 | -3 | 30 | 0.11 | 0.11
24 | 6 | 9 | -3 | 30 | 0.1 | 0.1
25 | 6 | 9 | -3 | 30 | 0.09 | 0.09
26 | 6 | 10 | -4 | 30 | 0.09 | 0.09
27 | 6 | 10 | -4 | 30 | 0.1 | 0.1
28 | 6 | 10 | -4 | 30 | 0.1 | 0.1
29 | 6 | 10 | -4 | 30 | 0.11 | 0.11
30 | 6 | 10 | -4 | 30 | 0.11 | 0.11
31 | 6 | 10 | -4 | 30 | 0.12 | 0.12
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME:Randy Stroud
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE:Randy Stroud |  | DATE:7/6/2025
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: (503)850-3576 |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Big Lake Youth Camp |  | ID#: 41 | 90958 | Month/Year: | 2025-06-01 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1 | 84 | 84 | 7.8 | 7.69 | 28.4983 | yes | 36
2 | 1 | 84 | 84 | 8 | 7.76 | 28.8335 | yes | 36
3 | 1 | 84 | 84 | 8.4 | 7.74 | 27.8637 | yes | 36
4 | 1 | 84 | 84 | 8.7 | 7.71 | 27.0138 | yes | 36
5 | 1 | 84 | 84 | 8.9 | 7.73 | 26.8446 | yes | 36
6 | 0.9 | 84 | 75.6 | 9.1 | 7.68 | 25.72 | yes | 36
7 | 0.9 | 84 | 75.6 | 9.3 | 7.65 | 25.1081 | yes | 36
8 | 0.9 | 84 | 75.6 | 9.6 | 7.67 | 24.7857 | yes | 36
9 | 0.9 | 84 | 75.6 | 9.8 | 7.69 | 24.6317 | yes | 36
10 | 0.8 | 84 | 67.2 | 10.2 | 7.72 | 23.9657 | yes | 36
11 | 0.8 | 84 | 67.2 | 10.5 | 7.75 | 23.7433 | yes | 36
12 | 0.8 | 84 | 67.2 | 10.7 | 7.78 | 23.68 | yes | 36
13 | 0.8 | 84 | 67.2 | 10.9 | 7.76 | 23.2029 | yes | 36
14 | 0.8 | 84 | 67.2 | 11.1 | 7.74 | 22.7363 | yes | 36
15 | 0.8 | 84 | 67.2 | 11.4 | 7.71 | 22.0556 | yes | 36
16 | 0.7 | 84 | 58.8 | 11.6 | 7.68 | 21.2975 | yes | 36
17 | 0.7 | 84 | 58.8 | 11.8 | 7.67 | 20.9461 | yes | 36
18 | 0.7 | 84 | 58.8 | 12 | 7.7 | 20.891 | yes | 36
19 | 0.7 | 84 | 58.8 | 12.1 | 7.72 | 20.9001 | yes | 36
20 | 0.7 | 84 | 58.8 | 12.2 | 7.75 | 20.9823 | yes | 36
21 | 0.7 | 84 | 58.8 | 12.3 | 7.77 | 20.9914 | yes | 36
22 | 0.7 | 84 | 58.8 | 12.4 | 7.79 | 21.0004 | yes | 36
23 | 0.7 | 84 | 58.8 | 12.6 | 7.76 | 20.4561 | yes | 36
24 | 0.7 | 84 | 58.8 | 12.7 | 7.71 | 19.9501 | yes | 36
25 | 0.6 | 84 | 50.4 | 12.9 | 7.73 | 19.6094 | yes | 36
26 | 1.8 | 84 | 151.2 | 13.1 | 7.74 | 22.2477 | yes | 36
27 | 1.8 | 84 | 151.2 | 13.3 | 7.72 | 21.7942 | yes | 36
28 | 1.7 | 84 | 142.8 | 13.5 | 7.69 | 21.032 | yes | 36
29 | 1.7 | 84 | 142.8 | 13.7 | 7.67 | 20.6029 | yes | 36
30 | 1.6 | 84 | 134.4 | 13.8 | 7.64 | 20.0139 | yes | 36
31 | 1.6 | 84 | 134.4 | 13.9 | 7.61 | 19.6631 | yes | 36
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised October 2013
PAGE 2 of 2