## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Linn
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2025-07-01
System Name: | Big Lake Youth Camp |  |  | ID#: 41 | 90958 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 6 | 12 | -6 | 30 | 0.1 | 0.1
2 | 6 | 12 | -6 | 30 | 0.11 | 0.11
3 | 6 | 14 | -8 | 30 | 0.12 | 0.12
4 | 6 | 14 | -8 | 30 | 0.13 | 0.13
5 | 6 | 16 | -10 | 30 | 0.14 | 0.14
6 | 6 | 16 | -10 | 30 | 0.15 | 0.15
7 | 6 | 17 | -11 | 30 | 0.16 | 0.16
8 | 7 | 17 | -10 | 30 | 0.17 | 0.17
9 | 7 | 18 | -11 | 30 | 0.19 | 0.19
10 | 7 | 18 | -11 | 30 | 0.24 | 0.24
11 | 7 | 18 | -11 | 30 | 0.26 | 0.26
12 | 7 | 19 | -12 | 30 | 0.29 | 0.29
13 | 7 | 19 | -12 | 30 | 0.31 | 0.31
14 | 8 | 19 | -11 | 30 | 0.35 | 0.35
15 | 8 | 19 | -11 | 30 | 0.3 | 0.3
16 | 8 | 19 | -11 | 30 | 0.25 | 0.25
17 | 8 | 19 | -11 | 30 | 0.23 | 0.23
18 | 8 | 19 | -11 | 30 | 0.22 | 0.22
19 | 8 | 19 | -11 | 30 | 0.21 | 0.21
20 | 8 | 20 | -12 | 30 | 0.23 | 0.23
21 | 8 | 20 | -12 | 30 | 0.25 | 0.25
22 | 8 | 20 | -12 | 30 | 0.28 | 0.28
23 | 8 | 20 | -12 | 30 | 0.3 | 0.3
24 | 8 | 20 | -12 | 30 | 0.32 | 0.32
25 | 9 | 21 | -12 | 30 | 0.34 | 0.34
26 | 9 | 21 | -12 | 30 | 0.37 | 0.37
27 | 9 | 21 | -12 | 30 | 0.35 | 0.35
28 | 9 | 21 | -12 | 30 | 0.33 | 0.33
29 | 9 | 22 | -13 | 30 | 0.31 | 0.31
30 | 9 | 22 | -13 | 30 | 0.28 | 0.28
31 | 9 | 22 | -13 | 30 | 0.26 | 0.26
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME:Randy Stroud
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE:Randy Stroud |  | DATE:8/9/2025
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: (503)850-3576 |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Big Lake Youth Camp |  | ID#: 41 | 90958 | Month/Year: | 2025-07-01 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.5 | 84 | 126 | 14.1 | 7.62 | 19.256 | Yes | 36
2 | 1.4 | 84 | 117.6 | 14.2 | 7.63 | 18.9828 | Yes | 36
3 | 1.4 | 84 | 117.6 | 14.3 | 7.61 | 18.7186 | Yes | 36
4 | 1.3 | 84 | 109.2 | 14.3 | 7.59 | 18.3714 | Yes | 36
5 | 1.3 | 84 | 109.2 | 14.4 | 7.57 | 18.1155 | Yes | 36
6 | 1.2 | 84 | 100.8 | 14.4 | 7.55 | 17.7792 | Yes | 36
7 | 1.2 | 84 | 100.8 | 15.2 | 8.02 | 20.0503 | Yes | 36
8 | 1.1 | 84 | 92.4 | 15.8 | 8.08 | 19.4767 | Yes | 36
9 | 1.1 | 84 | 92.4 | 16.3 | 8.15 | 19.3334 | Yes | 36
10 | 1.1 | 84 | 92.4 | 16.6 | 8.19 | 19.2338 | Yes | 36
11 | 1 | 84 | 84 | 16.9 | 8.2 | 18.7108 | Yes | 36
12 | 1 | 84 | 84 | 17.2 | 8.24 | 18.6143 | Yes | 36
13 | 1 | 84 | 84 | 17.5 | 8.29 | 18.5867 | Yes | 36
14 | 3 | 84 | 252 | 17.8 | 8.31 | 23.0188 | Yes | 36
15 | 2.7 | 84 | 226.8 | 17.7 | 7.93 | 19.4757 | Yes | 36
16 | 2.5 | 84 | 210 | 17.5 | 7.84 | 18.6638 | Yes | 36
17 | 2.3 | 84 | 193.2 | 17.3 | 7.79 | 18.1511 | Yes | 36
18 | 2.2 | 84 | 184.8 | 17.3 | 7.76 | 17.7485 | Yes | 36
19 | 2.1 | 84 | 176.4 | 17.4 | 7.73 | 17.2396 | Yes | 36
20 | 2 | 84 | 168 | 17.3 | 7.68 | 16.8444 | Yes | 36
21 | 2 | 84 | 168 | 17.3 | 7.65 | 16.6585 | Yes | 36
22 | 1.9 | 84 | 159.6 | 17.2 | 7.62 | 16.3972 | Yes | 36
23 | 1.9 | 84 | 159.6 | 17.1 | 7.64 | 16.6294 | Yes | 36
24 | 1.8 | 84 | 151.2 | 17 | 7.69 | 16.8601 | Yes | 36
25 | 1.8 | 84 | 151.2 | 16.9 | 7.71 | 17.0986 | Yes | 36
26 | 1.7 | 84 | 142.8 | 17.1 | 7.73 | 16.8056 | Yes | 36
27 | 1.7 | 84 | 142.8 | 17 | 7.75 | 17.0434 | Yes | 36
28 | 1.6 | 84 | 134.4 | 17.2 | 7.77 | 16.7513 | Yes | 36
29 | 1.5 | 84 | 126 | 17.3 | 7.79 | 16.5741 | Yes | 36
30 | 1.4 | 84 | 117.6 | 17.2 | 7.8 | 16.5573 | Yes | 36
31 | 1.4 | 84 | 117.6 | 17.1 | 7.82 | 16.7917 | Yes | 36
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised October 2013
PAGE 2 of 2