## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Linn
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2025-08-01
System Name: | Big Lake Youth Camp |  |  | ID#: 41 | 90958 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 4 | 6 | -2 | 30 | 0.25 | 0.25
2 | 4 | 6 | -2 | 30 | 0.27 | 0.27
3 | 4 | 6 | -2 | 30 | 0.3 | 0.3
4 | 4 | 6 | -2 | 30 | 0.35 | 0.35
5 | 4 | 6 | -2 | 30 | 0.38 | 0.38
6 | 4 | 6 | -2 | 30 | 0.41 | 0.41
7 | 4 | 6 | -2 | 30 | 0.44 | 0.44
8 | 4 | 6 | -2 | 30 | 0.47 | 0.47
9 | 4 | 6 | -2 | 30 | 0.51 | 0.51
10 | 6 | 8 | -2 | 30 | 0.12 | 0.12
11 | 6 | 8 | -2 | 30 | 0.14 | 0.14
12 | 6 | 8 | -2 | 30 | 0.16 | 0.16
13 | 6 | 8 | -2 | 30 | 0.19 | 0.19
14 | 6 | 8 | -2 | 30 | 0.21 | 0.21
15 | 6 | 8 | -2 | 30 | 0.23 | 0.23
16 | 6 | 10 | -4 | 30 | 0.25 | 0.25
17 | 6 | 10 | -4 | 30 | 0.28 | 0.28
18 | 6 | 10 | -4 | 30 | 0.26 | 0.26
19 | 6 | 10 | -4 | 30 | 0.29 | 0.29
20 | 8 | 12 | -4 | 30 | 0.31 | 0.31
21 | 8 | 12 | -4 | 30 | 0.33 | 0.33
22 | 8 | 12 | -4 | 30 | 0.35 | 0.35
23 | 8 | 12 | -4 | 30 | 0.32 | 0.32
24 | 8 | 12 | -4 | 30 | 0.34 | 0.34
25 | 8 | 14 | -6 | 30 | 0.36 | 0.36
26 | 8 | 14 | -6 | 30 | 0.38 | 0.38
27 | 8 | 14 | -6 | 30 | 0.4 | 0.4
28 | 8 | 14 | -6 | 30 | 0.42 | 0.42
29 | 8 | 14 | -6 | 30 | 0.44 | 0.44
30 | 8 | 16 | -8 | 30 | 0.47 | 0.47
31 | 8 | 16 | -8 | 30 | 0.45 | 0.45
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME:Randy Stroud
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE:Randy Stroud |  | DATE:9/9/2025
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: (503)850-3576 |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Big Lake Youth Camp |  | ID#: 41 | 90958 | Month/Year: | 2025-08-01 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.3 | 84 | 109.2 | 17.1 | 7.78 | 16.3579 | Yes | 36
2 | 1.3 | 84 | 109.2 | 17 | 7.75 | 16.2855 | Yes | 36
3 | 1.3 | 84 | 109.2 | 16.8 | 7.79 | 16.7499 | Yes | 36
4 | 1.2 | 84 | 100.8 | 16.7 | 7.81 | 16.7949 | Yes | 36
5 | 1.2 | 84 | 100.8 | 16.6 | 7.85 | 17.1589 | Yes | 36
6 | 1.2 | 84 | 100.8 | 16.4 | 7.86 | 17.4532 | Yes | 36
7 | 1.1 | 84 | 92.4 | 16.3 | 7.88 | 17.5 | Yes | 36
8 | 1.1 | 84 | 92.4 | 16.1 | 7.9 | 17.8658 | Yes | 36
9 | 1.1 | 84 | 92.4 | 16 | 7.93 | 18.1853 | Yes | 36
10 | 1 | 84 | 84 | 16.2 | 7.91 | 17.6119 | Yes | 36
11 | 1 | 84 | 84 | 16.1 | 7.89 | 17.599 | Yes | 36
12 | 1 | 84 | 84 | 16 | 7.87 | 17.586 | Yes | 36
13 | 1 | 84 | 84 | 16.1 | 7.84 | 17.2769 | Yes | 36
14 | 0.9 | 84 | 75.6 | 16.1 | 7.86 | 17.2084 | Yes | 36
15 | 0.9 | 84 | 75.6 | 16.1 | 7.83 | 17.0186 | Yes | 36
16 | 0.9 | 84 | 75.6 | 16 | 7.88 | 17.4517 | Yes | 36
17 | 2 | 84 | 168 | 16 | 7.86 | 19.626 | Yes | 36
18 | 2 | 84 | 168 | 16 | 7.84 | 19.4819 | Yes | 36
19 | 2 | 84 | 168 | 15.9 | 7.81 | 19.3959 | Yes | 36
20 | 2 | 84 | 168 | 15.9 | 7.79 | 19.2535 | Yes | 36
21 | 1.9 | 84 | 159.6 | 15.9 | 7.77 | 18.8965 | Yes | 36
22 | 1.9 | 84 | 159.6 | 15.8 | 7.75 | 18.8826 | Yes | 36
23 | 1.9 | 84 | 159.6 | 15.8 | 7.78 | 19.0927 | Yes | 36
24 | 1.9 | 84 | 159.6 | 15.8 | 7.79 | 19.1632 | Yes | 36
25 | 1.8 | 84 | 151.2 | 15.7 | 7.76 | 18.8635 | Yes | 36
26 | 1.8 | 84 | 151.2 | 15.7 | 7.74 | 18.7249 | Yes | 36
27 | 1.8 | 84 | 151.2 | 15.7 | 7.72 | 18.5873 | Yes | 36
28 | 1.8 | 84 | 151.2 | 15.6 | 7.7 | 18.5736 | Yes | 36
29 | 1.7 | 84 | 142.8 | 15.6 | 7.73 | 18.5685 | Yes | 36
30 | 1.7 | 84 | 142.8 | 15.6 | 7.75 | 18.706 | Yes | 36
31 | 1.7 | 84 | 142.8 | 15.5 | 7.78 | 19.0401 | Yes | 36
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised October 2013
PAGE 2 of 2