## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Linn
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2025-09-01
System Name: | Big Lake Youth Camp |  |  | ID#: 41 | 90958 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 8 | 16 | -8 | 30 | 0.43 | 0.43
2 | 8 | 16 | -8 | 30 | 0.46 | 0.46
3 | 8 | 16 | -8 | 30 | 0.47 | 0.47
4 | 8 | 18 | -10 | 30 | 0.48 | 0.48
5 | 8 | 18 | -10 | 30 | 0.49 | 0.49
6 | 10 | 18 | -8 | 30 | 0.47 | 0.47
7 | 10 | 20 | -10 | 30 | 0.45 | 0.45
8 | 10 | 20 | -10 | 30 | 0.42 | 0.42
9 | 4 | 6 | -2 | 30 | 0.29 | 0.29
10 | 4 | 6 | -2 | 30 | 0.28 | 0.28
11 | 4 | 6 | -2 | 30 | 0.3 | 0.3
12 | 4 | 6 | -2 | 30 | 0.27 | 0.27
13 | 4 | 6 | -2 | 30 | 0.25 | 0.25
14 | 4 | 6 | -2 | 30 | 0.28 | 0.28
15 | 4 | 6 | -2 | 30 | 0.26 | 0.26
16 | 4 | 6 | -2 | 30 | 0.23 | 0.23
17 | 4 | 6 | -2 | 30 | 0.21 | 0.21
18 | 4 | 6 | -2 | 30 | 0.19 | 0.19
19 | 6 | 6 | 0 | 30 | 0.16 | 0.16
20 | 6 | 6 | 0 | 30 | 0.14 | 0.14
21 | 6 | 6 | 0 | 30 | 0.12 | 0.12
22 | 6 | 6 | 0 | 30 | 0.15 | 0.15
23 | 6 | 6 | 0 | 30 | 0.13 | 0.13
24 | 6 | 6 | 0 | 30 | 0.1 | 0.1
25 | 6 | 6 | 0 | 30 | 0.12 | 0.12
26 | 6 | 6 | 0 | 30 | 0.14 | 0.14
27 | 6 | 6 | 0 | 30 | 0.17 | 0.17
28 | 6 | 6 | 0 | 30 | 0.21 | 0.21
29 | 6 | 6 | 0 | 30 | 0.25 | 0.25
30 | 6 | 6 | 0 | 30 | 0.27 | 0.27
31 |  |  |  | 30
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME:Randy Stroud
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE:Randy Stroud |  | DATE:10/1/2025
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: (503)850-3576 |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Big Lake Youth Camp |  | ID#: 41 | 90958 | Month/Year: | 2025-09-01 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.7 | 84 | 142.8 | 15.8 | 7.76 | 18.5273 | Yes | 36
2 | 1.7 | 84 | 142.8 | 15.6 | 7.78 | 18.9141 | Yes | 36
3 | 1.6 | 84 | 134.4 | 15.6 | 7.75 | 18.495 | Yes | 36
4 | 1.6 | 84 | 134.4 | 15.4 | 7.73 | 18.6046 | Yes | 36
5 | 1.6 | 84 | 134.4 | 15.4 | 7.71 | 18.4678 | Yes | 36
6 | 1.5 | 84 | 126 | 15.2 | 7.69 | 18.3676 | Yes | 36
7 | 1.5 | 84 | 126 | 15.2 | 7.65 | 18.0985 | Yes | 36
8 | 1.5 | 84 | 126 | 15.1 | 7.66 | 18.2865 | Yes | 36
9 | 1.4 | 84 | 117.6 | 15 | 7.68 | 18.3355 | Yes | 36
10 | 1.6 | 84 | 134.4 | 14.8 | 7.77 | 19.6482 | Yes | 36
11 | 1.6 | 84 | 134.4 | 14.6 | 7.79 | 20.0579 | Yes | 36
12 | 1.8 | 84 | 151.2 | 14.4 | 7.67 | 19.8924 | Yes | 36
13 | 1.8 | 84 | 151.2 | 14.2 | 7.7 | 20.382 | Yes | 36
14 | 1.9 | 84 | 159.6 | 14 | 7.72 | 21.0434 | Yes | 36
15 | 1.9 | 84 | 159.6 | 13.9 | 7.74 | 21.3398 | Yes | 36
16 | 2 | 84 | 168 | 13.7 | 7.73 | 21.79 | Yes | 36
17 | 2 | 84 | 168 | 13.6 | 7.75 | 22.0966 | Yes | 36
18 | 2 | 84 | 168 | 13.4 | 7.77 | 22.5563 | Yes | 36
19 | 2.1 | 84 | 176.4 | 13.2 | 7.79 | 23.2869 | Yes | 36
20 | 2.1 | 84 | 176.4 | 13 | 7.81 | 23.7709 | Yes | 36
21 | 2.1 | 84 | 176.4 | 12.8 | 7.84 | 24.354 | Yes | 36
22 | 2.2 | 84 | 184.8 | 12.6 | 7.86 | 25.1418 | Yes | 36
23 | 2.2 | 84 | 184.8 | 12.7 | 7.88 | 25.1602 | Yes | 36
24 | 2.2 | 84 | 184.8 | 12.5 | 7.9 | 25.6825 | Yes | 36
25 | 2.3 | 84 | 193.2 | 12.3 | 7.93 | 26.65 | Yes | 36
26 | 2.3 | 84 | 193.2 | 12.1 | 7.96 | 27.303 | Yes | 36
27 | 2.3 | 84 | 193.2 | 12.2 | 7.98 | 27.3151 | Yes | 36
28 | 2.4 | 84 | 201.6 | 12 | 8.04 | 28.6186 | Yes | 36
29 | 2.4 | 84 | 201.6 | 11.9 | 8.09 | 29.337 | Yes | 36
30 | 2.4 | 84 | 201.6 | 11.8 | 8.11 | 29.7505 | Yes | 36
31 |  | 84 | [5 empty] | 36
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised October 2013
PAGE 2 of 2