## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Linn
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2025-11-01
System Name: | Big Lake Youth Camp |  |  | ID#: 41 | 90958 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 12 | 18 | -6 | 30 | 0.43 | 0.43
2 | 12 | 18 | -6 | 30 | 0.41 | 0.41
3 | 12 | 20 | -8 | 30 | 0.4 | 0.4
4 | 12 | 20 | -8 | 30 | 0.39 | 0.39
5 | 12 | 20 | -8 | 30 | 0.39 | 0.39
6 | 12 | 22 | -10 | 30 | 0.41 | 0.41
7 | 12 | 22 | -10 | 30 | 0.42 | 0.42
8 | 12 | 22 | -10 | 30 | 0.39 | 0.39
9 | 12 | 22 | -10 | 30 | 0.38 | 0.38
10 | 12 | 24 | -12 | 30 | 0.38 | 0.38
11 | 12 | 24 | -12 | 30 | 0.37 | 0.37
12 | 12 | 24 | -12 | 30 | 0.36 | 0.36
13 | 12 | 24 | -12 | 30 | 0.35 | 0.35
14 | 14 | 26 | -12 | 30 | 0.34 | 0.34
15 | 14 | 26 | -12 | 30 | 0.33 | 0.33
16 | 14 | 26 | -12 | 30 | 0.32 | 0.32
17 | 14 | 26 | -12 | 30 | 0.34 | 0.34
18 | 14 | 26 | -12 | 30 | 0.33 | 0.33
19 | 14 | 28 | -14 | 30 | 0.32 | 0.32
20 | 14 | 28 | -14 | 30 | 0.31 | 0.31
21 | 14 | 28 | -14 | 30 | 0.3 | 0.3
22 | 14 | 30 | -16 | 30 | 0.29 | 0.29
23 | 14 | 30 | -16 | 30 | 0.28 | 0.28
24 | 14 | 30 | -16 | 30 | 0.27 | 0.27
25 | 14 | 30 | -16 | 30 | 0.26 | 0.26
26 | 4 | 8 | -4 | 30 | 0.24 | 0.24
27 | 4 | 8 | -4 | 30 | 0.23 | 0.23
28 | 4 | 8 | -4 | 30 | 0.22 | 0.22
29 | 4 | 8 | -4 | 30 | 0.2 | 0.2
30 | 6 | 10 | -4 | 30 | 0.19 | 0.19
31 |  |  |  | 30
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME:Randy Stroud
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE:Randy Stroud |  | DATE:12/9/2025
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: (503)850-3576 |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Big Lake Youth Camp |  | ID#: 41 | 90958 | Month/Year: | 2025-11-01 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.3 | 84 | 109.2 | 6 | 7.65 | 32.8698 | Yes | 36
2 | 1.3 | 84 | 109.2 | 6 | 7.63 | 32.6315 | Yes | 36
3 | 1.3 | 84 | 109.2 | 5.9 | 7.61 | 32.6169 | Yes | 36
4 | 1.3 | 84 | 109.2 | 5.9 | 7.58 | 32.263 | Yes | 36
5 | 1.2 | 84 | 100.8 | 5.8 | 7.62 | 32.577 | Yes | 36
6 | 1.2 | 84 | 100.8 | 5.8 | 7.6 | 32.3409 | Yes | 36
7 | 1.2 | 84 | 100.8 | 5.7 | 7.57 | 32.2091 | Yes | 36
8 | 1.2 | 84 | 100.8 | 5.7 | 7.54 | 31.86 | Yes | 36
9 | 1.2 | 84 | 100.8 | 5.6 | 7.59 | 32.6663 | Yes | 36
10 | 1.1 | 84 | 92.4 | 5.6 | 7.63 | 32.76 | Yes | 36
11 | 1.1 | 84 | 92.4 | 5.5 | 7.66 | 33.3468 | Yes | 36
12 | 1.1 | 84 | 92.4 | 5.5 | 7.69 | 33.7133 | Yes | 36
13 | 1.1 | 84 | 92.4 | 5.5 | 7.72 | 34.0842 | Yes | 36
14 | 1 | 84 | 84 | 5.4 | 7.75 | 34.2917 | Yes | 36
15 | 1 | 84 | 84 | 5.4 | 7.77 | 34.543 | Yes | 36
16 | 1 | 84 | 84 | 5.3 | 7.78 | 34.9078 | Yes | 36
17 | 2.6 | 84 | 218.4 | 5.3 | 7.81 | 42.6374 | Yes | 36
18 | 2.5 | 84 | 210 | 5.2 | 7.84 | 42.9004 | Yes | 36
19 | 2.5 | 84 | 210 | 5.2 | 7.86 | 43.219 | Yes | 36
20 | 2.3 | 84 | 193.2 | 5.1 | 7.83 | 42.0294 | Yes | 36
21 | 2 | 84 | 168 | 5.1 | 7.79 | 39.967 | Yes | 36
22 | 1.9 | 84 | 159.6 | 5 | 7.82 | 40.2126 | Yes | 36
23 | 1.7 | 84 | 142.8 | 5 | 7.86 | 39.8547 | Yes | 36
24 | 1.5 | 84 | 126 | 4.9 | 7.88 | 39.4822 | Yes | 36
25 | 1.3 | 84 | 109.2 | 4.9 | 7.91 | 38.9875 | Yes | 36
26 | 1.2 | 84 | 100.8 | 4.7 | 7.93 | 39.3536 | Yes | 36
27 | 1.2 | 84 | 100.8 | 4.7 | 7.95 | 39.6444 | Yes | 36
28 | 1.1 | 84 | 92.4 | 4.5 | 7.98 | 40.1647 | Yes | 36
29 | 1.1 | 84 | 92.4 | 4.4 | 7.99 | 40.5928 | Yes | 36
30 | 1 | 84 | 84 | 4.2 | 7.96 | 40.2263 | Yes | 36
31 |  | 84 | [5 empty] | 36
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised October 2013
PAGE 2 of 2