## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Linn
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2025-12-01
System Name: | Big Lake Youth Camp |  |  | ID#: 41 | 90958 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 6 | 10 | -4 | 30 | 0.19 | 0.19
2 | 6 | 10 | -4 | 30 | 0.19 | 0.19
3 | 6 | 10 | -4 | 30 | 0.19 | 0.19
4 | 6 | 10 | -4 | 30 | 0.19 | 0.19
5 | 6 | 10 | -4 | 30 | 0.2 | 0.2
6 | 6 | 10 | -4 | 30 | 0.2 | 0.2
7 | 6 | 10 | -4 | 30 | 0.2 | 0.2
8 | 6 | 10 | -4 | 30 | 0.2 | 0.2
9 | 6 | 10 | -4 | 30 | 0.21 | 0.21
10 | 6 | 10 | -4 | 30 | 0.21 | 0.21
11 | 6 | 10 | -4 | 30 | 0.21 | 0.21
12 | 6 | 10 | -4 | 30 | 0.21 | 0.21
13 | 8 | 12 | -4 | 30 | 0.21 | 0.21
14 | 8 | 12 | -4 | 30 | 0.22 | 0.22
15 | 8 | 12 | -4 | 30 | 0.22 | 0.22
16 | 8 | 12 | -4 | 30 | 0.23 | 0.23
17 | 8 | 12 | -4 | 30 | 0.23 | 0.23
18 | 8 | 12 | -4 | 30 | 0.23 | 0.23
19 | 8 | 12 | -4 | 30 | 0.24 | 0.24
20 | 8 | 12 | -4 | 30 | 0.24 | 0.24
21 | 8 | 12 | -4 | 30 | 0.25 | 0.25
22 | 8 | 12 | -4 | 30 | 0.25 | 0.25
23 | 8 | 12 | -4 | 30 | 0.25 | 0.25
24 | 8 | 14 | -6 | 30 | 0.26 | 0.26
25 | 8 | 14 | -6 | 30 | 0.26 | 0.26
26 | 8 | 14 | -6 | 30 | 0.27 | 0.27
27 | 8 | 14 | -6 | 30 | 0.27 | 0.27
28 | 8 | 14 | -6 | 30 | 0.28 | 0.28
29 | 8 | 14 | -6 | 30 | 0.28 | 0.28
30 | 8 | 14 | -6 | 30 | 0.28 | 0.28
31 | 8 | 14 | -6 | 30 | 0.29 | 0.29
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME:Randy Stroud
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE:Randy Stroud |  | DATE:1/10/2026
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: (503) |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Big Lake Youth Camp |  | ID#: 41 | 90958 | Month/Year: | 2025-12-01 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1 | 84 | 84 | 4 | 7.97 | 40.9375 | Yes | 36
2 | 1 | 84 | 84 | 3.8 | 7.98 | 41.6619 | Yes | 36
3 | 1 | 84 | 84 | 3.6 | 7.96 | 41.9325 | Yes | 36
4 | 1 | 84 | 84 | 3.5 | 7.95 | 42.0685 | Yes | 36
5 | 1 | 84 | 84 | 3.3 | 7.96 | 42.8141 | Yes | 36
6 | 1 | 84 | 84 | 3.1 | 7.97 | 43.5735 | Yes | 36
7 | 1 | 84 | 84 | 2.8 | 7.95 | 44.163 | Yes | 36
8 | 1.2 | 84 | 100.8 | 2.6 | 7.94 | 45.6915 | Yes | 36
9 | 1.2 | 84 | 100.8 | 2.4 | 7.93 | 46.1607 | Yes | 36
10 | 1.2 | 84 | 100.8 | 2.2 | 7.91 | 46.4621 | Yes | 36
11 | 1.2 | 84 | 100.8 | 2 | 7.92 | 47.2896 | Yes | 36
12 | 1.2 | 84 | 100.8 | 1.9 | 7.93 | 47.7979 | Yes | 36
13 | 1.2 | 84 | 100.8 | 1.9 | 7.95 | 48.1547 | Yes | 36
14 | 1 | 84 | 84 | 1.8 | 7.97 | 47.7003 | Yes | 36
15 | 1 | 84 | 84 | 1.8 | 7.99 | 48.0563 | Yes | 36
16 | 1 | 84 | 84 | 1.7 | 8.01 | 48.7543 | Yes | 36
17 | 1 | 84 | 84 | 1.7 | 7.98 | 48.2132 | Yes | 36
18 | 1.1 | 84 | 92.4 | 1.7 | 7.96 | 48.4313 | Yes | 36
19 | 1.1 | 84 | 92.4 | 1.6 | 7.97 | 48.9524 | Yes | 36
20 | 1.1 | 84 | 92.4 | 1.6 | 7.95 | 48.5895 | Yes | 36
21 | 1.2 | 84 | 100.8 | 1.6 | 7.93 | 48.8093 | Yes | 36
22 | 1.2 | 84 | 100.8 | 1.6 | 7.91 | 48.4475 | Yes | 36
23 | 1.2 | 84 | 100.8 | 1.5 | 7.89 | 48.4252 | Yes | 36
24 | 1.2 | 84 | 100.8 | 1.5 | 7.87 | 48.0664 | Yes | 36
25 | 1.2 | 84 | 100.8 | 1.5 | 7.88 | 48.2455 | Yes | 36
26 | 1.2 | 84 | 100.8 | 1.5 | 7.9 | 48.6057 | Yes | 36
27 | 1.3 | 84 | 109.2 | 1.5 | 7.92 | 49.5581 | Yes | 36
28 | 1.3 | 84 | 109.2 | 1.4 | 7.94 | 50.2789 | Yes | 36
29 | 1.3 | 84 | 109.2 | 1.4 | 7.95 | 50.4666 | Yes | 36
30 | 1.3 | 84 | 109.2 | 1.4 | 7.96 | 50.655 | Yes | 36
31 | 1.3 | 84 | 109.2 | 1.4 | 7.97 | 50.8442 | Yes | 36
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised October 2013
PAGE 2 of 2