## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Linn
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2026-01-01
System Name: | Big Lake Youth Camp |  |  | ID#: 41 | 90958 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 4 | 6 | -2 | 30 | 0.28 | 0.28
2 | 4 | 6 | -2 | 30 | 0.28 | 0.28
3 | 4 | 6 | -2 | 30 | 0.28 | 0.28
4 | 4 | 6 | -2 | 30 | 0.27 | 0.27
5 | 4 | 6 | -2 | 30 | 0.27 | 0.27
6 | 4 | 6 | -2 | 30 | 0.28 | 0.28
7 | 4 | 6 | -2 | 30 | 0.28 | 0.28
8 | 4 | 6 | -2 | 30 | 0.29 | 0.29
9 | 4 | 6 | -2 | 30 | 0.29 | 0.29
10 | 4 | 6 | -2 | 30 | 0.29 | 0.29
11 | 4 | 6 | -2 | 30 | 0.26 | 0.26
12 | 4 | 6 | -2 | 30 | 0.24 | 0.24
13 | 4 | 6 | -2 | 30 | 0.24 | 0.24
14 | 4 | 6 | -2 | 30 | 0.22 | 0.22
15 | 4 | 6 | -2 | 30 | 0.22 | 0.22
16 | 4 | 6 | -2 | 30 | 0.2 | 0.2
17 | 4 | 6 | -2 | 30 | 0.2 | 0.2
18 | 4 | 6 | -2 | 30 | 0.18 | 0.18
19 | 4 | 6 | -2 | 30 | 0.18 | 0.18
20 | 4 | 8 | -4 | 30 | 0.16 | 0.16
21 | 4 | 8 | -4 | 30 | 0.16 | 0.16
22 | 4 | 8 | -4 | 30 | 0.14 | 0.14
23 | 4 | 8 | -4 | 30 | 0.14 | 0.14
24 | 4 | 8 | -4 | 30 | 0.16 | 0.16
25 | 4 | 8 | -4 | 30 | 0.16 | 0.16
26 | 4 | 8 | -4 | 30 | 0.18 | 0.18
27 | 4 | 8 | -4 | 30 | 0.18 | 0.18
28 | 4 | 8 | -4 | 30 | 0.16 | 0.16
29 | 4 | 8 | -4 | 30 | 0.16 | 0.16
30 | 4 | 8 | -4 | 30 | 0.14 | 0.14
31 | 4 | 8 | -4 | 30 | 0.14 | 0.14
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME:Randy Stroud
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE:Randy Stroud |  | DATE:2/9/2026
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: (503)850-3576 |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Big Lake Youth Camp |  | ID#: 41 | 90958 | Month/Year: | 2026-01-01 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.1 | 84 | 92.4 | 1.4 | 7.89 | 48.1851 | Yes | 36
2 | 1.2 | 84 | 100.8 | 1.4 | 7.86 | 48.2233 | Yes | 36
3 | 1.2 | 84 | 100.8 | 1.4 | 7.83 | 47.6884 | Yes | 36
4 | 1.2 | 84 | 100.8 | 1.4 | 7.85 | 48.0443 | Yes | 36
5 | 1.3 | 84 | 109.2 | 1.4 | 7.88 | 49.1679 | Yes | 36
6 | 1.3 | 84 | 109.2 | 1.4 | 7.9 | 49.5353 | Yes | 36
7 | 1.3 | 84 | 109.2 | 1.4 | 7.92 | 49.9057 | Yes | 36
8 | 1.3 | 84 | 109.2 | 1.4 | 7.95 | 50.4666 | Yes | 36
9 | 1.3 | 84 | 109.2 | 1.5 | 7.96 | 50.302 | Yes | 36
10 | 1.3 | 84 | 109.2 | 1.5 | 7.98 | 50.6784 | Yes | 36
11 | 1.2 | 84 | 100.8 | 1.5 | 8.44 | 59.4721 | Yes | 36
12 | 1.2 | 84 | 100.8 | 1.5 | 8.82 | 68.6087 | Yes | 36
13 | 1.2 | 84 | 100.8 | 1.6 | 8.8 | 67.6135 | Yes | 36
14 | 1.2 | 84 | 100.8 | 1.6 | 8.64 | 63.6614 | Yes | 36
15 | 1.2 | 84 | 100.8 | 1.6 | 8.6 | 62.7112 | Yes | 36
16 | 1.2 | 84 | 100.8 | 1.6 | 8.57 | 62.0082 | Yes | 36
17 | 1.2 | 84 | 100.8 | 1.6 | 8.49 | 60.1732 | Yes | 36
18 | 1.2 | 84 | 100.8 | 1.6 | 8.46 | 59.4996 | Yes | 36
19 | 1.2 | 84 | 100.8 | 1.6 | 8.38 | 57.7414 | Yes | 36
20 | 1.1 | 84 | 92.4 | 1.7 | 8.35 | 56.0183 | Yes | 36
21 | 1.1 | 84 | 92.4 | 1.7 | 8.31 | 55.1861 | Yes | 36
22 | 1.1 | 84 | 92.4 | 1.7 | 8.27 | 54.3667 | Yes | 36
23 | 1.1 | 84 | 92.4 | 1.7 | 8.23 | 53.5601 | Yes | 36
24 | 1.1 | 84 | 92.4 | 1.7 | 8.17 | 52.3733 | Yes | 36
25 | 1.1 | 84 | 92.4 | 1.7 | 8.14 | 51.7903 | Yes | 36
26 | 1.1 | 84 | 92.4 | 1.8 | 8.08 | 50.2914 | Yes | 36
27 | 1 | 84 | 84 | 1.8 | 8.03 | 48.7766 | Yes | 36
28 | 1 | 84 | 84 | 1.8 | 7.97 | 47.7003 | Yes | 36
29 | 1 | 84 | 84 | 1.8 | 7.92 | 46.8223 | Yes | 36
30 | 1 | 84 | 84 | 1.8 | 7.88 | 46.1321 | Yes | 36
31 | 1 | 84 | 84 | 1.8 | 7.83 | 45.2843 | Yes | 36
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised October 2013
PAGE 2 of 2