## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Linn
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2026-02-01
System Name: | Big Lake Youth Camp |  |  | ID#: 41 | 90958 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 4 | 8 | -4 | 30 | 0.14 | 0.14
2 | 4 | 8 | -4 | 30 | 0.14 | 0.14
3 | 4 | 8 | -4 | 30 | 0.12 | 0.12
4 | 4 | 8 | -4 | 30 | 0.14 | 0.14
5 | 4 | 8 | -4 | 30 | 0.14 | 0.14
6 | 4 | 8 | -4 | 30 | 0.12 | 0.12
7 | 4 | 8 | -4 | 30 | 0.12 | 0.12
8 | 4 | 8 | -4 | 30 | 0.11 | 0.11
9 | 4 | 8 | -4 | 30 | 0.11 | 0.11
10 | 4 | 8 | -4 | 30 | 0.1 | 0.1
11 | 4 | 8 | -4 | 30 | 0.1 | 0.1
12 | 4 | 8 | -4 | 30 | 0.09 | 0.09
13 | 4 | 8 | -4 | 30 | 0.09 | 0.09
14 | 4 | 6 | -2 | 30 | 0.24 | 0.24
15 | 4 | 6 | -2 | 30 | 0.2 | 0.2
16 | 4 | 6 | -2 | 30 | 0.18 | 0.18
17 | 4 | 6 | -2 | 30 | 0.16 | 0.16
18 | 4 | 6 | -2 | 30 | 0.14 | 0.14
19 | 4 | 6 | -2 | 30 | 0.12 | 0.12
20 | 4 | 6 | -2 | 30 | 0.1 | 0.1
21 | 4 | 8 | -4 | 30 | 0.1 | 0.1
22 | 4 | 8 | -4 | 30 | 0.1 | 0.1
23 | 4 | 8 | -4 | 30 | 0.1 | 0.1
24 | 4 | 8 | -4 | 30 | 0.1 | 0.1
25 | 4 | 8 | -4 | 30 | 0.09 | 0.09
26 | 4 | 8 | -4 | 30 | 0.09 | 0.09
27 | 4 | 8 | -4 | 30 | 0.1 | 0.1
28 | 4 | 8 | -4 | 30 | 0.1 | 0.1
29 |  |  |  | 30
30 |  |  |  | 30
31 |  |  |  | 30
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME:Randy Stroud
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE:Randy Stroud |  | DATE:3/10/2026
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #:(503)850-3576 |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Big Lake Youth Camp |  | ID#: 41 | 90958 | Month/Year: | 2026-02-01 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1 | 84 | 84 | 1.8 | 7.86 | 45.791 | Yes | 36
2 | 1 | 84 | 84 | 1.8 | 7.81 | 44.9498 | Yes | 36
3 | 1 | 84 | 84 | 1.8 | 7.78 | 44.4528 | Yes | 36
4 | 1 | 84 | 84 | 1.8 | 7.74 | 43.7992 | Yes | 36
5 | 0.9 | 84 | 75.6 | 1.8 | 7.77 | 43.7647 | Yes | 36
6 | 0.9 | 84 | 75.6 | 1.8 | 7.79 | 44.0899 | Yes | 36
7 | 0.9 | 84 | 75.6 | 1.9 | 7.82 | 44.2737 | Yes | 36
8 | 0.9 | 84 | 75.6 | 1.9 | 7.87 | 45.1017 | Yes | 36
9 | 0.9 | 84 | 75.6 | 1.9 | 7.83 | 44.438 | Yes | 36
10 | 0.9 | 84 | 75.6 | 2 | 7.89 | 45.1223 | Yes | 36
11 | 0.9 | 84 | 75.6 | 2 | 7.91 | 45.4582 | Yes | 36
12 | 0.8 | 84 | 67.2 | 2.3 | 7.95 | 44.6493 | Yes | 36
13 | 0.8 | 84 | 67.2 | 2.5 | 8.16 | 47.6006 | Yes | 36
14 | 2.7 | 84 | 226.8 | 2.7 | 8.28 | 61.6732 | Yes | 36
15 | 2.5 | 84 | 210 | 2.4 | 8.22 | 60.1192 | Yes | 36
16 | 2.3 | 84 | 193.2 | 2.2 | 8.17 | 58.4135 | Yes | 36
17 | 2.1 | 84 | 176.4 | 2.1 | 8.07 | 55.3157 | Yes | 36
18 | 1.9 | 84 | 159.6 | 2 | 7.98 | 52.5843 | Yes | 36
19 | 1.7 | 84 | 142.8 | 2.2 | 7.95 | 50.0622 | Yes | 36
20 | 1.5 | 84 | 126 | 2.1 | 7.9 | 48.3138 | Yes | 36
21 | 1.3 | 84 | 109.2 | 2 | 7.87 | 46.9768 | Yes | 36
22 | 1.1 | 84 | 92.4 | 1.9 | 7.83 | 45.5093 | Yes | 36
23 | 1 | 84 | 84 | 1.9 | 7.88 | 45.812 | Yes | 36
24 | 1 | 84 | 84 | 1.9 | 7.84 | 45.1374 | Yes | 36
25 | 0.9 | 84 | 75.6 | 1.9 | 7.81 | 44.1101 | Yes | 36
26 | 0.9 | 84 | 75.6 | 1.7 | 7.86 | 45.5645 | Yes | 36
27 | 0.9 | 84 | 75.6 | 1.7 | 7.92 | 46.5904 | Yes | 36
28 | 0.9 | 84 | 75.6 | 1.6 | 7.95 | 47.4421 | Yes | 36
29 |  | 84 | [5 empty] | 36
30 |  | 84 | [5 empty] | 36
31 |  | 84 | [5 empty] | 36
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised October 2013
PAGE 2 of 2