## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | Tillamook
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2021-12-01
System Name: | OPRD Cape Lookout |  |  | ID#: 41 | 91068 |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  | 0.22 |  |  |  | 0.22
2 |  |  | 0.15 |  |  |  | 0.15
3 |  |  | 0.12 |  |  |  | 0.12
4 |  |  | 0.14 |  |  |  | 0.14
5 |  |  | 0.13 |  |  |  | 0.13
6 |  |  | 0.13 |  |  |  | 0.13
7 |  |  | 0.12 |  |  |  | 0.12
8 |  |  | 0.07 |  |  |  | 0.07
9 |  |  | 0.09 |  |  |  | 0.09
10 |  |  | 0.09 |  |  |  | 0.09
11 |  |  | 0.22 |  |  |  | 0.22
12 |  |  | 0.12 |  |  |  | 0.12
13 |  |  | 0.14 |  |  |  | 0.14
14 |  |  | 0.13 |  |  |  | 0.13
15 |  |  | 0.1 |  |  |  | 0.1
16 |  |  | 0.09 |  |  |  | 0.09
17 |  |  | 0.08 |  |  |  | 0.08
18 |  |  | 0.07 |  |  |  | 0.07
19 |  |  | 0.14 |  |  |  | 0.14
20 |  |  | 0.09 |  |  |  | 0.09
21 |  |  | 0.06 |  |  |  | 0.06
22 |  |  | 0.05 |  |  |  | 0.05
23 |  |  | 0.08 |  |  |  | 0.08
24 |  |  | 0.26 |  |  |  | 0.26
25 |  |  | 0.09 |  |  |  | 0.09
26 |  |  | 0.54 |  |  |  | 0.54
27 |  |  | 0.17 |  |  |  | 0.17
28 |  |  | 0.09 |  |  |  | 0.09
29 |  |  | 0.16 |  |  |  | 0.16
30 |  |  | 0.44 |  |  |  | 0.44
31 |  |  | 0.54 |  |  |  | 0.54
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
Notes: |  |  |  |  | PRINTED NAME: Shiloh Copenhaver
[5 empty] | SIGNATURE: |  |  | 2022-01-07
[5 empty] | PHONE #: ( 503 )842-3182 |  |  | CERT #:
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | OPRD Cape Lookout |  | ID#: 41 91068 |  | Month/Year: | 2021-01-21 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.48 | 50 | 74 | 9.4 | 6.97 | 41.9073 | Yes | 72
2 | 1.42 | 50 | 71 | 9.4 | 7.05 | 42.8077 | Yes | 72
3 | 1.33 | 50 | 66.5 | 8.9 | 6.94 | 42.137 | Yes | 72
4 | 1.05 | 50 | 52.5 | 8.9 | 6.98 | 41.4074 | Yes | 72
5 | 1.05 | 50 | 52.5 | 8.9 | 6.96 | 41.1193 | Yes | 72
6 | 1.27 | 50 | 63.5 | 8.9 | 7.01 | 42.8922 | Yes | 72
7 | 1.47 | 50 | 73.5 | 8.9 | 7.08 | 44.9648 | Yes | 72
8 | 1.43 | 50 | 71.5 | 8.9 | 7.08 | 44.7616 | Yes | 72
9 | 1.35 | 50 | 67.5 | 8.3 | 7 | 44.8704 | Yes | 72
10 | 1.34 | 50 | 67 | 8.3 | 7.05 | 45.6167 | Yes | 72
11 | 1.31 | 50 | 65.5 | 8.3 | 7.09 | 46.1083 | Yes | 72
12 | 1.24 | 50 | 62 | 8.3 | 7 | 44.3155 | Yes | 72
13 | 1.61 | 50 | 80.5 | 7.8 | 7 | 47.773 | Yes | 72
14 | 1.59 | 50 | 79.5 | 7.2 | 7 | 49.6086 | Yes | 72
15 | 1.49 | 50 | 74.5 | 7.2 | 7.06 | 50.1031 | Yes | 72
16 | 1.56 | 50 | 78 | 6.7 | 7.15 | 53.936 | Yes | 72
17 | 1.49 | 50 | 74.5 | 6.7 | 7.03 | 51.2562 | Yes | 72
18 | 1.28 | 50 | 64 | 6.7 | 7.04 | 50.2166 | Yes | 72
19 | 1.46 | 50 | 73 | 6.7 | 6.97 | 49.9996 | Yes | 72
20 | 1.41 | 50 | 70.5 | 6.7 | 6.96 | 49.5379 | Yes | 72
21 | 1.38 | 50 | 69 | 6.7 | 7.04 | 50.7949 | Yes | 72
22 | 1.27 | 50 | 63.5 | 6.7 | 7.14 | 51.9807 | Yes | 72
23 | 1.49 | 50 | 74.5 | 7.8 | 7.1 | 48.826 | Yes | 72 | 1
24 | 1.3 | 50 | 65 | 7.8 | 7.1 | 47.7795 | Yes | 72
25 | 1.5 | 50 | 75 | 7.8 | 7.15 | 49.7586 | Yes | 72
26 | 1.43 | 50 | 71.5 | 6.7 | 7.05 | 51.2694 | Yes | 72
27 | 1.4 | 50 | 70 | 6.1 | 7.14 | 54.9354 | Yes | 72
28 | 1.34 | 50 | 67 | 6.1 | 7.14 | 54.5566 | Yes | 72
29 | 1.31 | 50 | 65.5 | 6.1 | 6.98 | 51.3433 | Yes | 72
30 | 1.61 | 50 | 80.5 | 6.1 | 7.06 | 54.6891 | Yes | 72
31 | 1.77 | 50 | 88.5 | 6.1 | 7.2 | 58.5891 | Yes | 72
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised September 2016
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2