## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Curry
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2021-05-01
System Name: | Marial Lodge |  |  | ID#: 41 | 91205 | WTP ID: TP- | A
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 18 |  | 18 | 31 | 0.19
2 | 18 |  | 18 | 31 | 0.18
3 | 18 |  | 18 | 31 | 0.19
4 | 18 |  | 18 | 31 | 0.17
5 | 18 |  | 18 | 31 | 0.19
6 | 18 |  | 18 | 31 | 0.18
7 | 18 |  | 18 | 31 | 0.2
8 | 18 |  | 18 | 31 | 0.19
9 | 18 |  | 18 | 31 | 0.17
10 | 18 |  | 18 | 31 | 0.2
11 | 18 |  | 18 | 31 | 0.21
12 | 18 |  | 18 | 31 | 0.2
13 | 18 |  | 18 | 31 | 0.22
14 | 18 |  | 18 | 31 | 0.21
15 | 18 |  | 18 | 31 | 0.19
16 | 18 |  | 18 | 31 | 0.19
17 | 18 |  | 18 | 31 | 0.17
18 | 18 |  | 18 | 31 | 0.17
19 | 18 |  | 18 | 31 | 0.18
20 | 18 |  | 18 | 31 | 0.2
21 | 18 |  | 18 | 31 | 0.19
22 | 18 |  | 18 | 31 | 0.17
23 | 18 |  | 18 | 31 | 0.17
24 | 18 |  | 18 | 31 | 0.16
25 | 18 |  | 18 | 31 | 0.2
26 | 18 |  | 18 | 31 | 0.19
27 | 18 |  | 18 | 31 | 0.19
28 | 18 |  | 18 | 31 | 0.21
29 | 18 |  | 18 | 31 | 0.22
30 | 18 |  | 18 | 31 | 0.19
31 | 18 |  | 18 | 31 | 0.17
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Robert Biscarret
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: Electronic |  | DATE:10/01/2020
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: (541)226-3085 |  | CERT #: N/A
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | A
System Name: | Marial Lodge |  | ID#: 41 | 91205 | Month/Year: |  | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.8 | 50 | 40 | 15.1 | 6.97 | 26.1502 | YES
2 | 0.8 | 50 | 40 | 15 | 6.96 | 26.2283 | YES
3 | 0.6 | 50 | 30 | 15.3 | 6.93 | 24.8443 | YES
4 | 0.8 | 50 | 40 | 15.1 | 6.97 | 26.1502 | YES
5 | 0.6 | 50 | 30 | 15.2 | 7.1 | 26.6463 | YES
6 | 0.6 | 50 | 30 | 15.1 | 7.11 | 26.9254 | YES
7 | 0.6 | 50 | 30 | 15.3 | 6.99 | 25.4061 | YES
8 | 0.6 | 50 | 30 | 15.4 | 7.13 | 26.5868 | YES
9 | 0.7 | 50 | 35 | 15.2 | 6.98 | 25.7756 | YES
10 | 0.6 | 50 | 30 | 15.5 | 7 | 25.1611 | YES
11 | 0.6 | 50 | 30 | 15.3 | 7.21 | 27.5737 | YES
12 | 0.7 | 50 | 35 | 15.56 | 7.17 | 27.0048 | YES
13 | 0.7 | 50 | 35 | 15.5 | 7.13 | 26.7131 | YES
14 | 0.8 | 50 | 40 | 15.6 | 7.22 | 27.7534 | YES
15 | 0.7 | 50 | 35 | 15.6 | 7.23 | 27.5402 | YES
16 | 0.7 | 50 | 35 | 15.7 | 7.22 | 27.2549 | YES
17 | 0.7 | 50 | 35 | 15.5 | 7.26 | 28.0359 | YES
18 | 0.6 | 50 | 30 | 15.6 | 7.33 | 28.258 | YES
19 | 0.7 | 50 | 35 | 15.7 | 7.31 | 28.1819 | YES
20 | 0.6 | 50 | 30 | 15.7 | 7.28 | 27.5529 | YES
21 | 0.6 | 50 | 30 | 15.8 | 7.29 | 27.4711 | YES
22 | 0.6 | 50 | 30 | 15.6 | 7.26 | 27.5325 | YES
23 | 0.5 | 50 | 25 | 15.8 | 7.3 | 27.26 | NO
24 | 0.7 | 50 | 35 | 15.7 | 7.34 | 28.4977 | YES
25 | 0.6 | 50 | 30 | 15.9 | 7.27 | 27.0856 | YES
26 | 0.7 | 50 | 35 | 15.8 | 7.3 | 27.8903 | YES
27 | 0.7 | 50 | 35 | 15.9 | 7.3 | 27.7043 | YES
28 | 0.7 | 50 | 35 | 15.9 | 7.32 | 27.9109 | YES
29 | 0.7 | 50 | 35 | 16 | 7.14 | 25.9292 | YES
30 | 0.6 | 50 | 30 | 15.9 | 7.17 | 26.0963 | YES
31 | 0.6 | 50 | 30 | 16.1 | 7.26 | 26.626 | YES
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2