## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Curry
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2022-06-01
System Name: | Marial Lodge |  |  | ID#: 41 | 91205 | WTP ID: TP- | A
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 18 |  | 18 | 31 | 0.17
2 | 18 |  | 18 | 31 | 0.19
3 | 18 |  | 18 | 31 | 0.22
4 | 18 |  | 18 | 31 | 0.19
5 | 18 |  | 18 | 31 | 0.18
6 | 18 |  | 18 | 31 | 0.19
7 | 18 |  | 18 | 31 | 0.21
8 | 18 |  | 18 | 31 | 0.19
9 | 18 |  | 18 | 31 | 0.19
10 | 18 |  | 18 | 31 | 0.17
11 | 18 |  | 18 | 31 | 0.19
12 | 18 |  | 18 | 31 | 0.18
13 | 18 |  | 18 | 31 | 0.2
14 | 18 |  | 18 | 31 | 0.2
15 | 18 |  | 18 | 31 | 0.16
16 | 18 |  | 18 | 31 | 0.17
17 | 18 |  | 18 | 31 | 0.19
18 | 18 |  | 18 | 31 | 0.17
19 | 18 |  | 18 | 31 | 0.2
20 | 18 |  | 18 | 31 | 0.19
21 | 18 |  | 18 | 31 | 0.2
22 | 18 |  | 18 | 31 | 0.18
23 | 18 |  | 18 | 31 | 0.21
24 | 18 |  | 18 | 31 | 0.2
25 | 18 |  | 18 | 31 | 0.22
26 | 18 |  | 18 | 31 | 0.17
27 | 18 |  | 18 | 31 | 0.17
28 | 18 |  | 18 | 31 | 0.19
29 | 18 |  | 18 | 31 | 0.17
30 | 18 |  | 18 | 31 | 0.18
31
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Robert Biscarret
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: Electronic |  | DATE:06/01/2022
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: (541)226-3085 |  | CERT #: N/A
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | A
System Name: | Marial Lodge |  | ID#: 41 | 91205 | Month/Year: | 2022-06-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.7 | 50 | 35 | 16.1 | 6.36 | 19.2349 | YES
2 | 0.6 | 50 | 30 | 16.4 | 6.31 | 18.2827 | YES
3 | 0.6 | 50 | 30 | 16.1 | 6.42 | 19.4477 | YES
4 | 0.7 | 50 | 35 | 16.3 | 6.4 | 19.2637 | YES
5 | 0.8 | 50 | 40 | 16.4 | 6.39 | 19.2836 | YES
6 | 0.8 | 50 | 40 | 16.4 | 6.44 | 19.6497 | YES
7 | 0.8 | 50 | 40 | 16.3 | 6.41 | 19.5613 | YES
8 | 0.8 | 50 | 40 | 16.5 | 6.38 | 19.0814 | YES
9 | 0.6 | 50 | 30 | 16.5 | 6.38 | 18.6446 | YES
10 | 0.8 | 50 | 40 | 16.4 | 6.37 | 19.139 | YES
11 | 0.8 | 50 | 40 | 16.7 | 6.42 | 19.1101 | YES
12 | 0.7 | 50 | 35 | 16.6 | 6.39 | 18.805 | YES
13 | 0.7 | 50 | 35 | 16.5 | 6.44 | 19.2927 | YES
14 | 0.6 | 50 | 30 | 16.6 | 6.47 | 19.157 | YES
15 | 0.6 | 50 | 30 | 16.8 | 6.43 | 18.6164 | YES
16 | 0.6 | 50 | 30 | 17 | 6.44 | 18.4348 | YES
17 | 0.7 | 50 | 35 | 17.1 | 6.48 | 18.8048 | YES
18 | 0.8 | 50 | 40 | 17 | 6.42 | 18.7253 | YES
19 | 0.8 | 50 | 40 | 17.3 | 6.4 | 18.2101 | YES
20 | 0.8 | 50 | 40 | 17.2 | 6.46 | 18.7535 | YES
21 | 0.8 | 50 | 40 | 17 | 6.49 | 19.2254 | YES
22 | 0.7 | 50 | 35 | 17.3 | 6.45 | 18.3428 | YES
23 | 0.8 | 50 | 40 | 17.4 | 6.44 | 18.3618 | YES
24 | 0.6 | 50 | 30 | 17.3 | 6.43 | 17.995 | YES
25 | 0.7 | 50 | 35 | 17.4 | 6.47 | 18.3566 | YES
26 | 0.6 | 50 | 30 | 17.5 | 6.5 | 18.2272 | YES
27 | 0.6 | 50 | 30 | 17.5 | 6.44 | 17.8192 | YES
28 | 0.7 | 50 | 35 | 17.6 | 6.65 | 19.3795 | YES
29 | 0.7 | 50 | 35 | 17.4 | 6.51 | 18.6354 | YES
30 | 0.7 | 50 | 35 | 17.5 | 6.63 | 19.365 | YES
31
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2