## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Curry
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2022-08-01
System Name: | Marial Lodge |  |  | ID#: 41 | 91205 | WTP ID: TP- | A
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 18 |  | 18 | 31 | 0.19
2 | 18 |  | 18 | 31 | 0.21
3 | 18 |  | 18 | 31 | 0.2
4 | 18 |  | 18 | 31 | 0.21
5 | 18 |  | 18 | 31 | 0.19
6 | 18 |  | 18 | 31 | 0.18
7 | 18 |  | 18 | 31 | 0.22
8 | 18 |  | 18 | 31 | 0.2
9 | 18 |  | 18 | 31 | 0.2
10 | 18 |  | 18 | 31 | 0.19
11 | 18 |  | 18 | 31 | 0.2
12 | 18 |  | 18 | 31 | 0.23
13 | 18 |  | 18 | 31 | 0.22
14 | 18 |  | 18 | 31 | 0.21
15 | 18 |  | 18 | 31 | 0.2
16 | 18 |  | 18 | 31 | 0.17
17 | 18 |  | 18 | 31 | 0.19
18 | 18 |  | 18 | 31 | 0.18
19 | 18 |  | 18 | 31 | 0.2
20 | 18 |  | 18 | 31 | 0.23
21 | 18 |  | 18 | 31 | 0.23
22 | 18 |  | 18 | 31 | 0.2
23 | 18 |  | 18 | 31 | 0.23
24 | 18 |  | 18 | 31 | 0.2
25 | 18 |  | 18 | 31 | 0.21
26 | 18 |  | 18 | 31 | 0.19
27 | 18 |  | 18 | 31 | 0.17
28 | 18 |  | 18 | 31 | 0.18
29 | 18 |  | 18 | 31 | 0.18
30 | 18 |  | 18 | 31 | 0.21
31 | 18 |  | 18 | 31 | 0.22
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Robert Biscarret
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: Electronic |  | 2022-08-01
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: (541)226-3085 |  | CERT #: N/A
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | A
System Name: | Marial Lodge |  | ID#: 41 | 91205 | Month/Year: | 2022-08-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.6 | 50 | 30 | 17.9 | 7.29 | 23.8618 | YES
2 | 0.6 | 50 | 30 | 18.1 | 7.38 | 24.3475 | YES
3 | 0.6 | 50 | 30 | 17.8 | 7.4 | 25.0289 | YES
4 | 0.7 | 50 | 35 | 18.4 | 7.36 | 23.9575 | YES
5 | 0.6 | 50 | 30 | 18.3 | 7.27 | 23.0555 | YES
6 | 0.7 | 50 | 35 | 18.7 | 7.32 | 23.1308 | YES
7 | 0.7 | 50 | 35 | 18 | 7.33 | 24.3362 | YES
8 | 0.8 | 50 | 40 | 18.8 | 7.3 | 23.0681 | YES
9 | 0.7 | 50 | 35 | 18.8 | 7.3 | 22.8045 | YES
10 | 0.6 | 50 | 30 | 19.3 | 7.38 | 22.4593 | YES
11 | 0.6 | 50 | 30 | 19.2 | 7.34 | 22.2752 | YES
12 | 0.6 | 50 | 30 | 19.3 | 7.27 | 21.5532 | YES
13 | 0.6 | 50 | 30 | 19.6 | 7.29 | 21.2801 | YES
14 | 0.7 | 50 | 35 | 19.4 | 7.28 | 21.7376 | YES
15 | 0.7 | 50 | 35 | 19.7 | 7.31 | 21.5429 | YES
16 | 0.7 | 50 | 35 | 19.5 | 7.33 | 21.9996 | YES
17 | 0.6 | 50 | 30 | 19.8 | 7.26 | 20.7598 | YES
18 | 0.8 | 50 | 40 | 19 | 7.81 | 27.5254 | YES
19 | 0.8 | 50 | 40 | 19.9 | 7.77 | 25.5318 | YES
20 | 0.7 | 50 | 35 | 19.7 | 7.68 | 24.738 | YES
21 | 0.8 | 50 | 40 | 20 | 7.53 | 23.1886 | YES
22 | 0.9 | 50 | 45 | 19.9 | 7.55 | 23.7918 | YES
23 | 0.9 | 50 | 45 | 20.3 | 7.55 | 23.1602 | YES
24 | 0.7 | 50 | 35 | 20.4 | 7.49 | 21.9827 | YES
25 | 0.6 | 50 | 30 | 20.2 | 7.47 | 21.8617 | YES
26 | 0.6 | 50 | 30 | 20.6 | 7.54 | 21.8452 | YES
27 | 0.7 | 50 | 35 | 20.8 | 7.51 | 21.5585 | YES
28 | 0.6 | 50 | 30 | 20.8 | 7.53 | 21.4719 | YES
29 | 0.6 | 50 | 30 | 21.1 | 7.4 | 20.0394 | YES
30 | 0.7 | 50 | 35 | 21.3 | 6.97 | 17.0068 | YES
31 | 0.6 | 50 | 30 | 21.6 | 7.81 | 22.5931 | YES
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2