## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Curry
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2022-08-01
System Name: | Marial Lodge |  |  | ID#: 41 | 91205 | WTP ID: TP- | A
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 18 |  | 18 | 31 | 0.2
2 | 18 |  | 18 | 31 | 0.17
3 | 18 |  | 18 | 31 | 0.17
4 | 18 |  | 18 | 31 | 0.17
5 | 18 |  | 18 | 31 | 0.19
6 | 18 |  | 18 | 31 | 0.19
7 | 18 |  | 18 | 31 | 0.2
8 | 18 |  | 18 | 31 | 0.21
9 | 18 |  | 18 | 31 | 0.19
10 | 18 |  | 18 | 31 | 0.22
11 | 18 |  | 18 | 31 | 0.18
12 | 18 |  | 18 | 31 | 0.21
13 | 18 |  | 18 | 31 | 0.19
14 | 18 |  | 18 | 31 | 0.19
15 | 18 |  | 18 | 31 | 0.18
16 | 18 |  | 18 | 31 | 0.17
17 | 18 |  | 18 | 31 | 0.17
18 | 18 |  | 18 | 31 | 0.19
19 | 18 |  | 18 | 31 | 0.23
20 | 18 |  | 18 | 31 | 0.2
21 | 18 |  | 18 | 31 | 0.22
22 | 18 |  | 18 | 31 | 0.21
23 | 18 |  | 18 | 31 | 0.22
24 | 18 |  | 18 | 31 | 0.21
25 | 18 |  | 18 | 31 | 0.19
26 | 18 |  | 18 | 31 | 0.17
27 | 18 |  | 18 | 31 | 0.19
28 | 18 |  | 18 | 31 | 0.2
29 | 18 |  | 18 | 31 | 0.2
30 | 18 |  | 18 | 31 | 0.22
31 | 18 |  | 18 | 31 | 0.2
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Robert Biscarret
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: Electronic |  | DATE: 8/31/22
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: (541)226-3085 |  | CERT #: N/A
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | A
System Name: | Marial Lodge |  | ID#: 41 | 91205 | Month/Year: | 2022-08-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.6 | 50 | 30 | 21.7 | 6.66 | 14.5394 | YES
2 | 0.6 | 50 | 30 | 21.9 | 6.39 | 12.9334 | YES
3 | 0.7 | 50 | 35 | 21.9 | 6.63 | 14.3452 | YES
4 | 0.8 | 50 | 40 | 22 | 6.51 | 13.7693 | YES
5 | 0.7 | 50 | 35 | 21.8 | 6.67 | 14.666 | YES
6 | 0.7 | 50 | 35 | 22 | 6.72 | 14.7444 | YES
7 | 0.6 | 50 | 30 | 22 | 6.69 | 14.4069 | YES
8 | 0.7 | 50 | 35 | 22.1 | 6.74 | 14.7556 | YES
9 | 0.7 | 50 | 35 | 22 | 6.77 | 15.0278 | YES
10 | 0.6 | 50 | 30 | 22.3 | 6.73 | 14.33 | YES
11 | 0.6 | 50 | 30 | 22.7 | 6.68 | 13.6773 | YES
12 | 0.6 | 50 | 30 | 22.6 | 6.75 | 14.1452 | YES
13 | 0.7 | 50 | 35 | 22.4 | 6.79 | 14.733 | YES
14 | 0.6 | 50 | 30 | 22.9 | 6.88 | 14.5612 | YES
15 | 0.6 | 50 | 30 | 23 | 6.81 | 14.0804 | YES
16 | 0.6 | 50 | 30 | 23.2 | 7.13 | 15.6886 | YES
17 | 0.8 | 50 | 40 | 23.1 | 7.11 | 16.047 | YES
18 | 0.8 | 50 | 40 | 23.4 | 6.96 | 14.8496 | YES
19 | 0.7 | 50 | 35 | 23.6 | 6.97 | 14.5319 | YES
20 | 0.8 | 50 | 40 | 23.4 | 6.91 | 14.5694 | YES
21 | 0.6 | 50 | 30 | 23.7 | 6.99 | 14.3734 | YES
22 | 0.6 | 50 | 30 | 23.8 | 7.21 | 15.5224 | YES
23 | 0.7 | 50 | 35 | 24 | 7.19 | 15.3741 | YES
24 | 0.7 | 50 | 35 | 24.2 | 7.18 | 15.1074 | YES
25 | 0.7 | 50 | 35 | 23.9 | 7.2 | 15.5386 | YES
26 | 0.8 | 50 | 40 | 24.3 | 7.252 | 15.602 | YES
27 | 0.6 | 50 | 30 | 24 | 7.22 | 15.3697 | YES
28 | 0.6 | 50 | 30 | 24.6 | 7.18 | 14.5274 | YES
29 | 0.7 | 50 | 35 | 24.7 | 7.24 | 14.9357 | YES
30 | 0.8 | 50 | 40 | 24.5 | 6.99 | 13.9274 | YES
31 | 0.8 | 50 | 40 | 24.9 | 7.21 | 14.7365 | YES
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2