## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Curry
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2023-05-01
System Name: | Marial Lodge |  |  | ID#: 41 | 91205 | WTP ID: TP- | A
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 18 |  | 18 | 31 | 0.18
2 | 18 |  | 18 | 31 | 0.19
3 | 18 |  | 18 | 31 | 0.19
4 | 18 |  | 18 | 31 | 0.17
5 | 18 |  | 18 | 31 | 0.19
6 | 18 |  | 18 | 31 | 0.18
7 | 18 |  | 18 | 31 | 0.2
8 | 18 |  | 18 | 31 | 0.19
9 | 18 |  | 18 | 31 | 0.17
10 | 18 |  | 18 | 31 | 0.2
11 | 18 |  | 18 | 31 | 0.21
12 | 18 |  | 18 | 31 | 0.2
13 | 18 |  | 18 | 31 | 0.22
14 | 18 |  | 18 | 31 | 0.21
15 | 18 |  | 18 | 31 | 0.19
16 | 18 |  | 18 | 31 | 0.19
17 | 18 |  | 18 | 31 | 0.17
18 | 18 |  | 18 | 31 | 0.17
19 | 18 |  | 18 | 31 | 0.17
20 | 18 |  | 18 | 31 | 0.18
21 | 18 |  | 18 | 31 | 0.19
22 | 18 |  | 18 | 31 | 0.2
23 | 18 |  | 18 | 31 | 0.17
24 | 18 |  | 18 | 31 | 0.18
25 | 18 |  | 18 | 31 | 0.17
26 | 18 |  | 18 | 31 | 0.17
27 | 18 |  | 18 | 31 | 0.16
28 | 18 |  | 18 | 31 | 0.178
29 | 18 |  | 18 | 31 | 0.18
30 | 18 |  | 18 | 31 | 0.2
31 | 18 |  | 18 | 31 | 0.18
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Robert Biscarret
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: Electronic |  | DATE: 5/31/2023
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: (541)226-3085 |  | CERT #: N/A
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | A
System Name: | Marial Lodge |  | ID#: 41 | 91205 | Month/Year: | 2023-05-31 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.8 | 50 | 40 | 13.7 | 7 | 29.0409 | YES
2 | 0.8 | 50 | 40 | 13.9 | 6.97 | 28.3378 | YES
3 | 0.6 | 50 | 30 | 14.2 | 6.96 | 27.0463 | YES
4 | 0.8 | 50 | 40 | 14.1 | 6.93 | 27.5487 | YES
5 | 0.6 | 50 | 30 | 14.6 | 6.97 | 26.4294 | YES
6 | 0.6 | 50 | 30 | 14.9 | 7.1 | 27.1871 | YES
7 | 0.6 | 50 | 30 | 15.3 | 7.11 | 26.5671 | YES
8 | 0.6 | 50 | 30 | 14.9 | 6.99 | 26.0969 | YES
9 | 0.8 | 50 | 40 | 15.2 | 7.13 | 27.5685 | YES
10 | 0.7 | 50 | 35 | 15.6 | 6.98 | 25.0931 | YES
11 | 0.7 | 50 | 35 | 15.6 | 7 | 25.2808 | YES
12 | 0.6 | 50 | 30 | 15.8 | 7.21 | 26.6658 | YES
13 | 0.6 | 50 | 30 | 15.7 | 7.17 | 26.4485 | YES
14 | 0.7 | 50 | 35 | 16.1 | 7.13 | 25.6602 | YES
15 | 0.6 | 50 | 30 | 16 | 7.22 | 26.409 | YES
16 | 0.8 | 50 | 40 | 16.4 | 7.26 | 26.7002 | YES
17 | 0.8 | 50 | 40 | 16.2 | 7.23 | 26.76 | YES
18 | 0.7 | 50 | 35 | 16.6 | 7.31 | 26.5342 | YES
19 | 0.6 | 50 | 30 | 16.3 | 7.33 | 26.9648 | YES
20 | 0.7 | 50 | 35 | 16.9 | 7.28 | 25.7171 | YES
21 | 0.7 | 50 | 35 | 16.8 | 7.29 | 25.9867 | YES
22 | 0.7 | 50 | 35 | 17.4 | 7.26 | 24.6839 | YES
23 | 0.7 | 50 | 35 | 17.7 | 7.3 | 24.5552 | YES
24 | 0.6 | 50 | 30 | 17.5 | 7.34 | 24.9732 | YES
25 | 0.8 | 50 | 40 | 17.7 | 7.27 | 24.562 | YES
26 | 0.6 | 50 | 30 | 17.7 | 7.3 | 24.2751 | YES
27 | 0.6 | 50 | 30 | 17.9 | 7.31 | 24.0406 | YES
28 | 0.8 | 50 | 40 | 17.6 | 7.14 | 23.5565 | YES
29 | 0.8 | 50 | 40 | 17.9 | 7.17 | 23.3461 | YES
30 | 0.7 | 50 | 35 | 17.8 | 7.26 | 24.0294 | YES
31 | 0.8 | 50 | 40 | 18 | 7.33 | 24.6169 | YES
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
PAGE 2 of 2