## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Curry
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2023-09-01
System Name: | Marial Lodge |  |  | ID#: 41 | 91205 | WTP ID: TP- | A
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 18 |  | 18 | 31 | 0.2
2 | 18 |  | 18 | 31 | 0.19
3 | 18 |  | 18 | 31 | 0.19
4 | 18 |  | 18 | 31 | 0.18
5 | 18 |  | 18 | 31 | 0.19
6 | 18 |  | 18 | 31 | 0.17
7 | 18 |  | 18 | 31 | 0.2
8 | 18 |  | 18 | 31 | 0.21
9 | 18 |  | 18 | 31 | 0.22
10 | 18 |  | 18 | 31 | 0.22
11 | 18 |  | 18 | 31 | 0.22
12 | 18 |  | 18 | 31 | 0.2
13 | 18 |  | 18 | 31 | 0.21
14 | 18 |  | 18 | 31 | 0.19
15 | 18 |  | 18 | 31 | 0.2
16 | 18 |  | 18 | 31 | 0.18
17 | 18 |  | 18 | 31 | 0.18
18 | 18 |  | 18 | 31 | 0.17
19 | 18 |  | 18 | 31 | 0.18
20 | 18 |  | 18 | 31 | 0.19
21 | 18 |  | 18 | 31 | 0.17
22 | 18 |  | 18 | 31 | 0.17
23 | 18 |  | 18 | 31 | 0.18
24 | 18 |  | 18 | 31 | 0.17
25 | 18 |  | 18 | 31 | 0.2
26 | 18 |  | 18 | 31 | 0.19
27 | 18 |  | 18 | 31 | 0.21
28 | 18 |  | 18 | 31 | 0.2
29 | 18 |  | 18 | 31 | 0.21
30 | 18 |  | 18 | 31 | 0.21
31 | 18 |  | 18 | 31
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Robert Biscarret
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: Electronic |  | DATE:09/01/2023
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: (541)226-3085 |  | CERT #: N/A
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | A
System Name: | Marial Lodge |  | ID#: 41 | 91205 | Month/Year: 09/2023 |  | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.8 | 50 | 40 | 19.3 | 7.46 | 23.6791 | YES
2 | 0.8 | 50 | 40 | 19 | 7.43 | 23.8924 | YES
3 | 0.8 | 50 | 40 | 19 | 7.43 | 23.8924 | YES
4 | 0.6 | 50 | 30 | 18.7 | 7.77 | 27.0438 | YES
5 | 0.7 | 50 | 35 | 18.8 | 7.79 | 27.3751 | YES
6 | 0.8 | 50 | 40 | 18.4 | 7.62 | 26.6991 | YES
7 | 0.7 | 50 | 35 | 18.9 | 7.6 | 25.3357 | YES
8 | 0.7 | 50 | 35 | 18.2 | 7.56 | 26.1607 | YES
9 | 0.8 | 50 | 40 | 18.3 | 7.51 | 25.8003 | YES
10 | 0.8 | 50 | 40 | 17.9 | 7.63 | 27.7108 | YES
11 | 0.9 | 50 | 45 | 17.9 | 7.49 | 26.6076 | YES
12 | 1 | 50 | 50 | 18 | 7.43 | 26.1437 | YES
13 | 0.6 | 50 | 30 | 17.5 | 7.44 | 25.9212 | YES
14 | 0.6 | 50 | 30 | 17.1 | 7.48 | 27.0246 | YES
15 | 0.7 | 50 | 35 | 16.8 | 7.48 | 27.8897 | YES
16 | 0.8 | 50 | 40 | 16.9 | 7.49 | 28.1263 | YES
17 | 0.8 | 50 | 40 | 16.8 | 7.4 | 27.3838 | YES
18 | 0.8 | 50 | 40 | 16.8 | 7.39 | 27.2822 | YES
19 | 0.7 | 50 | 35 | 16.8 | 7.41 | 27.1734 | YES
20 | 0.7 | 50 | 35 | 16.4 | 7.43 | 28.1188 | YES
21 | 0.8 | 50 | 40 | 16.3 | 7.42 | 28.5264 | YES
22 | 0.8 | 50 | 40 | 16.4 | 7.5 | 29.1905 | YES
23 | 0.7 | 50 | 35 | 15.9 | 7.53 | 30.1734 | YES
24 | 0.8 | 50 | 40 | 15.6 | 7.49 | 30.6783 | YES
25 | 0.8 | 50 | 40 | 15.7 | 7.46 | 30.1372 | YES
26 | 0.8 | 50 | 40 | 15.4 | 7.54 | 31.6715 | YES
27 | 0.8 | 50 | 40 | 15.2 | 7.57 | 32.455 | YES
28 | 0.8 | 50 | 40 | 14.9 | 7.52 | 32.5033 | YES
29 | 0.7 | 50 | 35 | 14.9 | 7.61 | 33.2237 | YES
30 | 0.8 | 50 | 40 | 14.8 | 7.73 | 35.3618 | YES
31 |  | 50
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2