## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Curry
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2024-05-24
System Name: | Marial Lodge |  |  | ID#: 41 | 91205 | WTP ID: TP- | A
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 18 |  | 18 | 31 | 0.17
2 | 18 |  | 18 | 31 | 0.19
3 | 18 |  | 18 | 31 | 0.17
4 | 18 |  | 18 | 31 | 0.18
5 | 18 |  | 18 | 31 | 0.2
6 | 18 |  | 18 | 31 | 0.2
7 | 18 |  | 18 | 31 | 0.17
8 | 18 |  | 18 | 31 | 0.18
9 | 18 |  | 18 | 31 | 0.19
10 | 18 |  | 18 | 31 | 0.2
11 | 18 |  | 18 | 31 | 0.19
12 | 18 |  | 18 | 31 | 0.19
13 | 18 |  | 18 | 31 | 0.17
14 | 18 |  | 18 | 31 | 0.19
15 | 18 |  | 18 | 31 | 0.18
16 | 18 |  | 18 | 31 | 0.18
17 | 18 |  | 18 | 31 | 0.18
18 | 18 |  | 18 | 31 | 0.2
19 | 18 |  | 18 | 31 | 0.22
20 | 18 |  | 18 | 31 | 0.2
21 | 18 |  | 18 | 31 | 0.19
22 | 18 |  | 18 | 31 | 0.2
23 | 18 |  | 18 | 31 | 0.18
24 | 18 |  | 18 | 31 | 0.19
25 | 18 |  | 18 | 31 | 0.17
26 | 18 |  | 18 | 31 | 0.19
27 | 18 |  | 18 | 31 | 0.17
28 | 18 |  | 18 | 31 | 0.18
29 | 18 |  | 18 | 31 | 0.18
30 | 18 |  | 18 | 31 | 0.17
31 | 18 |  | 18 | 31 | 0.17
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: Robert Biscarret
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: Electronic |  | DATE:5/24
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: (541)226-3085 |  | CERT #: N/A
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | A
System Name: | Marial Lodge |  | ID#: 41 | 91205 | Month/Year: |  | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.6 | 50 | 30 | 12.2 | 6.6 | 28.0578 | YES
2 | 0.6 | 50 | 30 | 11.9 | 6.4 | 26.7628 | YES
3 | 0.6 | 50 | 30 | 13.2 | 6.7 | 26.2537 | YES
4 | 0.5 | 50 | 25 | 13.4 | 6.4 | 22.8968 | YES
5 | 0.6 | 50 | 30 | 13.1 | 6.8 | 27.4318 | YES
6 | 0.7 | 50 | 35 | 13.7 | 7.1 | 29.7967 | YES
7 | 0.7 | 50 | 35 | 13 | 7 | 30.0858 | YES
8 | 0.8 | 50 | 40 | 14.6 | 7.2 | 29.4527 | YES
9 | 0.6 | 50 | 30 | 14.1 | 6.8 | 25.6541 | YES
10 | 0.6 | 50 | 30 | 15.2 | 6.6 | 22.1109 | YES
11 | 0.6 | 50 | 30 | 14.3 | 6.9 | 26.2726 | YES
12 | 0.6 | 50 | 30 | 13.9 | 6.9 | 26.9862 | YES
13 | 0.7 | 50 | 35 | 12.6 | 7 | 30.8998 | YES
14 | 0.7 | 50 | 35 | 13.3 | 7.2 | 31.758 | YES
15 | 0.6 | 50 | 30 | 14 | 6.9 | 26.8061 | YES
16 | 0.8 | 50 | 40 | 14 | 7.1 | 29.5406 | YES
17 | 0.8 | 50 | 40 | 14.8 | 7.1 | 28.0024 | YES
18 | 0.8 | 50 | 40 | 15.3 | 7.3 | 29.1695 | YES
19 | 0.8 | 50 | 40 | 14.7 | 7 | 27.1619 | YES
20 | 0.6 | 50 | 30 | 15.2 | 6.8 | 23.8275 | YES
21 | 0.7 | 50 | 35 | 14.8 | 7.3 | 29.8182 | YES
22 | 0.6 | 50 | 30 | 15.2 | 7.1 | 26.6463 | YES
23 | 0.7 | 50 | 35 | 13.1 | 7.2 | 32.1843 | YES
24 | 0.7 | 50 | 35 | 12.2 | 7.1 | 33.5359 | YES
25 | 0.8 | 50 | 40 | 14.4 | 7.7 | 35.9148 | YES
26 | 0.7 | 50 | 35 | 11.6 | 7.1 | 34.8477 | YES
27 | 0.7 | 50 | 35 | 12.9 | 7.2 | 32.6161 | YES
28 | 0.8 | 50 | 40 | 15.1 | 7.8 | 35.5712 | YES
29 | 0.8 | 50 | 40 | 13.3 | 7.5 | 35.8891 | YES
30 | 0.7 | 50 | 35 | 13.6 | 7.2 | 31.129 | YES
31 | 0.8 | 50 | 40 | 17.5 | 7.6 | 28.1469 | YES
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2