## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Jackson
Cartridge or Bag Filtration | [5 empty] | Month/Year: | May/2023
System Name: |  |  |  | ID#: 41 |  | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]Highest Reading of the day 1 [NTU]
1 | 21 | 19 | 2 | 25 | 0.013 | 0.01
2 | 19 | 16 | 3 | 25 | 0.01 | 0.01
3 | 19 | 16 | 3 | 25 | 0.01 | 0.01
4 | 45 | 43 | 2 | 25 | 0.01 | 0.01
5 | 9 | 7 | 2 | 25 | 0.01 | 0.01
6 | 10 | 7 | 3 | 25 | 0.01 | 0.01
7 | 9 | 4 | 5 | 25 | 0.01 | 0.01
8 | 11 | 8 | 3 | 25 | 0.01 | 0.01
9 | 32 | 30 | 2 | 25 | 0.01 | 0.01
10 | 10 | 7 | 3 | 25 | 0.01 | 0.01
11 | 9 | 6 | 3 | 25 | 0.01 | 0.01
12 | 10 | 7 | 3 | 25 | 0.01 | 0.01
13 | 9 | 7 | 2 | 25 | 0.01 | 0.01
14 | 9 | 7 | 2 | 25 | 0.01 | 0.01
15 | 8 | 6 | 2 | 25 | 0.01 | 0.01
16 | 8 | 6 | 2 | 25 | 0.01 | 0.01
17 | 8 | 6 | 2 | 25 | 0.01 | 0.01
18 | 8 | 6 | 2 | 25 | 0.01 | 0.01
19 | 8 | 6 | 2 | 25 | 0.01 | 0.01
20 | 8 | 6 | 2 | 25 | 0.01 | 0.01
21 | 8 | 6 | 2 | 25 | 0.01 | 0.01
22 | 8 | 6 | 2 | 25 | 0.01 | 0.01
23 | 7 | 5 | 2 | 25 | 0.01 | 0.01
24 | 8 | 6 | 2 | 25 | 0.01 | 0.01
25 | 45 | 43 | 2 | 25 | 3.6 | 3.6
26 | 45 | 45 | 0 | 25 | 1 | 1
27 | 45 | 45 | 0 | 25 | 1.17 | 1.17
28 | 45 | 45 | 0 | 25 | 0.01 | 0.01
29 | 35 | 33 | 2 | 25 | 0.01 | 0.01
30 | 24 | 22 | 2 | 25 | 0.01 | 0.01
31 | 21 | 19 | 2 | 25 | 0.01 | 0.01
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | yes | yes | yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME:Cedar Hursh
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | Cedar Hursh |  | 2023-06-07
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | 5416606072 |  | none
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Cascade Gorge Properties |  | ID#: 41 |  | Month/Year: | 2023-05-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2Minimum Cl2 Residual at 1st User ( C ) 2Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T)Contact Time (T)Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2CT Met? 2CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] | pH | formula | Yes / No | [GPM]
1 | 2.4 | 207 | 496.8 | 14.5 | 7.3 | 36.9088 | YES | 2.5
2 | 3.5 | 207 | 724.5 | 13.5 | 7.2 | 43.0578 | YES | 2.5
3 | 3.5 | 207 | 724.5 | 13.2 | 7.2 | 43.9218 | YES | 2.5
4 | 3.5 | 207 | 724.5 | 12.5 | 7.3 | 47.7255 | YES | 4.9
5 | 3.5 | 207 | 724.5 | 12.8 | 7.3 | 46.7881 | YES | 2
6 | 3.5 | 207 | 724.5 | 12.5 | 7.3 | 47.7255 | YES | 2
7 | 3.5 | 207 | 724.5 | 12.1 | 7.1 | 46.1183 | YES | 2
8 | 3.5 | 207 | 724.5 | 12.9 | 7.2 | 44.8027 | YES | 2.2
9 | 3.5 | 207 | 724.5 | 14 | 7 | 38.6965 | YES | 4.2
10 | 3.5 | 207 | 724.5 | 13.3 | 7.1 | 42.0559 | YES | 3
11 | 3.4 | 207 | 703.8 | 13.8 | 7.2 | 41.7356 | YES | 3
12 | 3.5 | 207 | 724.5 | 15.7 | 7.2 | 37.2118 | YES | 3
13 | 3.5 | 207 | 724.5 | 16.3 | 7.2 | 35.7572 | YES | 2
14 | 3.5 | 207 | 724.5 | 18 | 7.2 | 31.9311 | YES | 2
15 | 3.5 | 207 | 724.5 | 18.1 | 7.2 | 31.719 | YES | 2
16 | 3.5 | 207 | 724.5 | 17.6 | 7.3 | 34.0292 | YES | 2
17 | 3.5 | 207 | 724.5 | 18.5 | 7.2 | 30.884 | YES | 1.7
18 | 3.5 | 207 | 724.5 | 18.3 | 7.2 | 31.2988 | YES | 1.9
19 | 3.5 | 207 | 724.5 | 18.2 | 7.1 | 30.3621 | YES | 2
20 | 3.5 | 207 | 724.5 | 18.8 | 7.1 | 29.1695 | YES | 2
21 | 3.5 | 207 | 724.5 | 17.5 | 7.2 | 33.0129 | YES | 1.5
22 | 3.5 | 207 | 724.5 | 18.2 | 7.2 | 31.5082 | YES | 1.5
23 | 3.5 | 207 | 724.5 | 16.4 | 7.5 | 39.6765 | YES | 1.5
24 | 3.5 | 207 | 724.5 | 17.3 | 7.1 | 32.2404 | YES | 1.5
25 | 3.5 | 207 | 724.5 | 17.5 | 7.1 | 31.8135 | YES | 1.5
26 | 3.5 | 207 | 724.5 | 17.5 | 7.1 | 31.8135 | YES | 1.5
27 | 3.5 | 207 | 724.5 | 17 | 7 | 31.6962 | YES | 1.5
28 | 3.5 | 207 | 724.5 | 17 | 7 | 31.6962 | YES | 1.5
29 | 3.5 | 207 | 724.5 | 16.8 | 7.5 | 38.6373 | YES | 3.8
30 | 3.5 | 207 | 724.5 | 17.2 | 7.4 | 36.2617 | YES | 2.5
31 | 3.5 | 207 | 724.5 | 15.8 | 7.3 | 38.3542 | YES | 2.5
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2