## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Jackson
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2023-10-23
System Name: | Cascade Gorge Properties |  |  | ID#: 91556 |  | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]Highest Reading of the day 1 [NTU]
1 |  |  |  | 25 | 0.372 | 0.372
2 |  |  |  | 25 | 0.37 | 0.37
3 |  |  |  | 25 | 0.36 | 0.36
4 |  |  |  | 25 | 0.36 | 0.36
5 |  |  |  | 25 | 0.36 | 0.36
6 | 44 | 42 | 2 | 25 | 0.37 | 0.37
7 | 44 | 42 | 2 | 25 | 0.375 | 0.375
8 |  |  |  | 25 | 0.366 | 0.366
9 |  |  |  | 25 | 0.363 | 0.363
10 |  |  |  | 25 | 0.357 | 0.357
11 |  |  |  | 25 | 0.35 | 0.35
12 |  |  |  | 25 | 0.357 | 0.357
13 |  |  |  | 25 | 0.35 | 0.35
14 |  |  |  | 25 | 0.345 | 0.345
15 |  |  |  | 25 | 0.345 | 0.345
16 |  |  |  | 25 | 0.35 | 0.35
17 |  |  |  | 25 | 0.34 | 0.34
18 |  |  |  | 25 | 0.339 | 0.339
19 |  |  |  | 25 | 0.341 | 0.341
20 |  |  |  | 25 | 0.342 | 0.342
21 |  |  |  | 25 | 0.337 | 0.337
22 |  |  |  | 25 | 0.341 | 0.341
23 |  |  |  | 25 | 0.336 | 0.336
24 | 44 | 42 | 2 | 25 | 0.05 | 0.05
25 |  |  |  | 25 | 0.047 | 0.047
26 |  |  |  | 25 | 0.05 | 0.05
27 |  |  |  | 25 | 0.047 | 0.047
28 |  |  |  | 25 | 0.05 | 0.05
29 |  |  |  | 25 | 0.046 | 0.046
30 | 46 | 44 | 2 | 25 | 0.05 | 0.05
31 | 46 | 44 | 2 | 25 | 0.05 | 0.05
Cartridge & Bag Filtration
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | YES
Notes: PSI = pounds per square inch |  |  |  |  | Cedar Hursh
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | CT's met everyday? (see back) |  | 2023-08-01
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. | [6 empty] | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Cascade Gorge Properties |  | ID#: 41 | 91556 | Month/Year: | 2023-02-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2Minimum Cl2 Residual at 1st User ( C ) 2Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T)Contact Time (T)Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2CT Met? 2CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 2.5 | 207 | 517.5 | 15.9 | 7.9 | 42.4349 | Yes
2 | 2 | 207 | 414 | 15.4 | 7.8 | 39.9528 | Yes
3 | 2.5 | 207 | 517.5 | 16.2 | 7.8 | 40.0957 | Yes
4 | 2 | 207 | 414 | 16.2 | 7.8 | 37.887 | YES
5 | 1.8 | 207 | 372.6 | 17 | 7.8 | 35.1192 | YES
6 | 1.8 | 207 | 372.6 | 18.3 | 7.8 | 32.2074 | YES | 4.5
7 | 1.5 | 207 | 310.5 | 17.4 | 7.9 | 34.2951 | YES | 4.5
8 | 1.5 | 207 | 310.5 | 17.5 | 7.7 | 31.6377 | YES
9 | 2 | 207 | 414 | 17.3 | 7.8 | 35.2163 | YES
10 | 1.5 | 207 | 310.5 | 16.4 | 7.6 | 32.8072 | YES
11 | 1.5 | 207 | 310.5 | 14.9 | 7.8 | 39.0258 | YES
12 | 1.5 | 207 | 310.5 | 14.5 | 7.8 | 40.0753 | YES
13 | 2.5 | 207 | 517.5 | 15.3 | 7.8 | 42.5605 | YES
14 | 1.5 | 207 | 310.5 | 14.5 | 7.8 | 40.0753 | YES
15 | 3 | 207 | 621 | 16 | 7.8 | 42.9964 | YES
16 | 3 | 207 | 621 | 16.2 | 7.8 | 42.4306 | YES
17 | 2.8 | 207 | 579.6 | 14.6 | 7.8 | 46.1169 | YES
18 | 1.5 | 207 | 310.5 | 15.7 | 7.8 | 37.007 | YES
19 | 1.5 | 207 | 310.5 | 15.8 | 7.8 | 36.7619 | YES
20 | 1.5 | 207 | 310.5 | 16.6 | 7.8 | 34.8578 | YES
21 | 2 | 207 | 414 | 16.1 | 7.8 | 38.1394 | YES
22 | 1.5 | 207 | 310.5 | 15.2 | 7.7 | 36.8711 | YES
23 | 2 | 207 | 414 | 13.8 | 7.8 | 44.4211 | YES
24 | 3 | 207 | 621 | 14 | 7.8 | 49.0789 | YES | 4.5
25 | 2 | 207 | 414 | 12.5 | 7.8 | 48.4098 | YES
26 | 2 | 207 | 414 | 13 | 7.8 | 46.8357 | YES
27 | 1.5 | 207 | 310.5 | 11.7 | 7.7 | 46.6493 | YES | 2.5
28 | 1.5 | 207 | 310.5 | 11.7 | 7.7 | 46.6493 | YES
29 | 1.5 | 207 | 310.5 | 11.7 | 7.7 | 46.6493 | YES
30 | 1.5 | 207 | 310.5 | 11.5 | 7.6 | 45.6312 | YES | 2.5
31 | 1.3 | 207 | 269.1 | 11.1 | 7.8 | 49.1684 | YES | 2.5
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2