## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | Jackson
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2023-10-23
System Name: | Cascade Gorge Properties |  |  | ID#: 91556 |  | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]Highest Reading of the day 1 [NTU]
1 | 46 | 44 | 2 | 25 | 0.046 | 0.046
2 |  |  |  | 25 | 0.05 | 0.05
3 | 46 | 44 | 2 | 25 | 0.05 | 0.05
4 | 46 | 44 | 2 | 25 | 0.05 | 0.05
5 | 46 | 44 | 2 | 25 | 0.05 | 0.05
6 |  |  |  | 25 | 0.05 | 0.05
7 | 46 | 44 | 2 | 25 | 0.047 | 0.047
8 | 46 | 44 | 2 | 25 | 0.05 | 0.05
9 | 46 | 44 | 2 | 25 | 0.05 | 0.05
10 | 46 | 44 | 2 | 25 | 0.05 | 0.05
11 | 46 | 44 | 2 | 25 | 0.05 | 0.05
12 | 46 | 44 | 2 | 25 | 0.05 | 0.05
13 |  |  |  | 25 | 0.05 | 0.05
14 |  |  |  | 25 | 0.05 | 0.05
15 |  |  |  | 25 | 0.05 | 0.05
16 |  |  |  | 25 | 0.05 | 0.05
17 | 46 | 44 | 2 | 25 | 0.05 | 0.05
18 | 46 | 44 | 2 | 25 | 0.05 | 0.05
19 |  |  |  | 25 | 0.05 | 0.05
20 | 46 | 44 | 2 | 25 | 0.05 | 0.05
21 | 46 | 44 | 2 | 25 | 0.05 | 0.05
22 |  |  |  | 25 | 0.05 | 0.05
23 | 46 | 44 | 2 | 25 | 0.05 | 0.05
24 |  |  |  | 25 | 0.05 | 0.05
25 |  |  |  | 25 | 0.05 | 0.05
26 | 46 | 44 | 2 | 25 | 0.05 | 0.05
27 | 46 | 44 | 2 | 25 | 0.05 | 0.05
28 | 46 | 44 | 2 | 25 | 0.05 | 0.05
29 | 46 | 44 | 2 | 25 | 0.05 | 0.05
30 | 46 | 44 | 2 | 25 | 0.05 | 0.05
31
Cartridge & Bag Filtration
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | YES
Notes: PSI = pounds per square inch |  |  |  |  | Cedar Hursh
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | CT's met everyday? (see back) |  | 2023-11-01
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. | [6 empty] | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Cascade Gorge Properties |  | ID#: 41 | 91556 | Month/Year: | 2023-11-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2Minimum Cl2 Residual at 1st User ( C ) 2Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T)Contact Time (T)Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2CT Met? 2CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.5 | 207 | 310.5 | 11.9 | 7.6 | 44.44 | Yes | 2.5
2 | 1.8 | 207 | 372.6 | 12.5 | 7.6 | 43.9755 | Yes
3 | 2 | 207 | 414 | 13.8 | 7.6 | 41.2701 | Yes | 2.5
4 | 2.5 | 207 | 517.5 | 13.9 | 7.6 | 43.3837 | YES | 2.5
5 | 2 | 207 | 414 | 13.4 | 7.7 | 43.9665 | YES | 2.5
6 | 1.5 | 207 | 310.5 | 12.3 | 7.7 | 44.8318 | YES
7 | 1 | 207 | 207 | 11.7 | 7.6 | 42.5597 | YES | 2.5
8 | 2.3 | 207 | 476.1 | 12.8 | 7.7 | 47.3242 | YES | 2.5
9 | 0.5 | 207 | 103.5 | 10.8 | 7.7 | 44.2075 | YES | 2.5
10 | 0.7 | 207 | 144.9 | 11.1 | 7.7 | 44.3316 | YES | 2.5
11 | 0.5 | 207 | 103.5 | 9.9 | 7.4 | 42.2201 | YES | 2.5
12 | 3.5 | 207 | 724.5 | 12.3 | 7.8 | 58.429 | YES | 2.5
13 | 1.5 | 207 | 310.5 | 11.2 | 7.6 | 46.5477 | YES
14 | 2 | 207 | 414 | 10.1 | 7.4 | 49.3891 | YES
15 | 2.5 | 207 | 517.5 | 11.7 | 7.6 | 50.4627 | YES
16 | 3.5 | 207 | 724.5 | 12.6 | 7.7 | 54.9029 | YES
17 | 3.5 | 207 | 724.5 | 12.3 | 7.6 | 54.3728 | YES | 2.5
18 | 3 | 207 | 621 | 12.1 | 7.6 | 52.0279 | YES | 2.5
19 | 3 | 207 | 621 | 11.9 | 7.6 | 52.7308 | YES
20 | 3 | 207 | 621 | 11.1 | 7.8 | 59.8064 | YES | 2.5
21 | 3 | 207 | 621 | 11.3 | 7.8 | 59.001 | YES | 2.5
22 | 3 | 207 | 621 | 11 | 7.8 | 60.2135 | YES
23 | 3 | 207 | 621 | 10.9 | 7.7 | 58.4724 | YES | 2.5
24 | 2.5 | 207 | 517.5 | 10.9 | 7.7 | 55.1865 | YES
25 | 3 | 207 | 621 | 11.1 | 7.8 | 59.8064 | YES
26 | 3 | 207 | 621 | 8.6 | 7.7 | 68.3874 | YES | 2.5
27 | 2.5 | 207 | 517.5 | 7.2 | 7.9 | 76.3856 | YES | 2.5
28 | 2.3 | 207 | 476.1 | 7 | 7.8 | 72.915 | YES | 2.5
29 | 2 | 207 | 414 | 7.4 | 7.9 | 71.0321 | YES | 2.5
30 | 3 | 207 | 621 | 8.8 | 7.8 | 69.9653 | YES | 2.5
31 |  | 207
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2